ACRONYM CMS-700 / Circuit Monitoring System

# GENERAL INFORMATION

Circuit monitoring system is multichannel measurement system for branch monitoring of low voltage electrical installations, which should brings a complete overview of the system performaces. Each system consists of a Control Unit and sensors, selected between different measurement ranges and mounting possibilities.

The circuit monitoring system should collect information both form the mains and form the sensors directly connected to every branch.

The input information from sensors must be transmitted throught a 4-pin flat cable, flexible in length. The number of sensors that could be monitored might be up to 3x32. The positioning of the sensors must be fully flexible and should allow for customized use.

The circuit monitoring system shall enable to measure the voltage, current, active, reactive and apparent power, power factor and total harmonic distortion from the mains and calculate energy and power for branches (using branch currents, mains voltage and power factor).

The opearting frequency must be from 45 Hz to 65 Hz in order to enable the device installation in different kind of application.

Measured data must be visualized remotely trought a digital communication with different protocols, in order to be suitable for the most common control systems: Modbus RTU, TCP or SNMP v1 and v2 and the encrypted v3. The two interfaces - LAN and RS485 – should guarantee a straightforward integration into any IT infrastructure.

To better supervise the power system there sould be available an integrated web-user interface, not only for the visualisation of the output values but also for the monitoring of system parameters. Measured data should be exported automatically to CSV files, mail or ftp, depending on the user preferernces. The circuit monitoring system should be configured trough the Web User Interface.

The circuit monitoring system should be equipped with two LEDs, one related to the status of the device and a one to the status of the network to enable a local monitoring.

# STANDARDS, MARKS, CERTIFICATION

The circuit monitoring system shall conform to the following international standards:

- Degree of protection: IEC 60259, IP20

- Electrical safety: IEC 61010-1, UL 508, CSA C22.2 No.14

# ELECTRICAL and MECHANICAL PROPERTIES

The circuit monitoring system should have the following mechanical and electrical properties that determine its use and employment:

- Installation in all energy distribution systems, in low voltage, single-phase, three-phase with neutral, balanced and unbalanced networks

- Must always be installed with current transformers with 5 A secondary average

- Includes a power supply with voltage range from 80 V to 277 V AC and frequency range from 45 Hz to 65 Hz

- Power consumption 40 VA max

- Type of AC measurement sampling

- Measured parameters from mains:

  - Voltage

  - Current

  - Power factor

  - THD

  - Active, reactive and apparent power

  - Energy

- Calculated parameters for branches:

  - Power

  - Energy

- Accuracy classes:

  - Voltage ± 1%

  - Current mains input ± 1%

  - Current ± 0.5% FS solid-core sensor

  - Current ± 1.0% FS open-core sensor

  - Power factor ± 0.2%

  - Active power ± 2%

  - Active energy ± 2%

- Measuring range:

  - Voltage mains direct 80 to 277 V AC TRMS with resolution 0.01 V

  - Power factor with resolution 0.01

  - Current inputs always external CT, primary up to 6,000 A AC, 5 A secondary (min. 60 mA)

  - Total harmonic distortion measure in the band up to 2,000 Hz

- Specification of the terminals:

  - Current and voltage inputs section 0.5 mm²  - 2.5 mm²

  - RS485 serial port 0.5 mm²  - 2.5 mm²

  - Ethernet port RJ45

- Overall dimensions: 161.5 mm x 87.0 mm x 64.9 mm

- Degree of protection IP20

- The circuit monitoring system will be equipped of technical installation manual available in the following languages:  English, Italian, German, French, Spanish, Chinese and Russian

# ENVIRONMENTAL FEATURES

The circuit monitoring system may ensure the installation and storage under the following environmental conditions:

- Storage temperature range from -40°C to +85°C

- Operating temperature range from -25°C to +60°C

- Relative humidity max 95% at 55°C

# ACCESSORIES – SENSORS

Sensors are necessary components of the measuring system, since they collect and send information form the branches. Sensors should be able to measure all types of current, whether AC, DC or mixed, in TRMS, enabling exact and effective measurements.

Every sensor should be equipped with a signal microprocessor, as measurement data could be transmitted digitally trough the CMS-bus interface to the control unit, reducing, as a consequence, the the number of cables into the distribution units and maximizing the security of the transmitted measurement..

The range of sensor should be flexible to every kind of installation. To integrate the sensors within PDUs there must be four different mounting variants available.

The The size of sensors must be contained in order to not waste space, not exceeding 25 mm width.

The range from which sensors must be selected should be varied. They can be divided in different groups depending on:

- Shape:

  - Open-core sensor

  - Closed-core sensor

- Tipe of application:

  - System pro M, SMISSLINE: For all LS, FI 6 FI-LS with twin terminals

  - S800: For all S800 devices with cage terminals

  - DIN rail: Universally usable

  - Cable tie: Universally usable

- Overall dimension:

  - 18-mm overall width

  - 25-mm overall width

- Mesasurement range:

  - Measuremnet range: 20 A, 40 A, 80 A, 160 A

The Table 1.1 resumes the total range of possible sensors, classified in according to shape, type of application and overall dimension:

| Sensors | System pro M, SMISSLINE | S800 | DIN rail | Cable tie |
| --- | --- | --- | --- | --- |
|  | For all LS, FI 6 FI-LS with twin terminals | For all S800 devices with cage terminals | Universally usable | Universally usable |
| Open-core sensors |  |  |  |  |
| 18-mm overall width | CMS-120PS CMS-121PS CMS-122PS | - | CMS-120DR CMS-121DR CMS-122DR | CMS-120CA CMS-121CA CMS-122CA |
| Solid-core sensors |  |  |  |  |
| 18-mm overall width | CMS-100PS CMS-101PS CMS-102PS | CMS-100S8 CMS-101S8 CMS-102S8 | CMS-100DR CMS-101DR CMS-102DR | CMS-100CA CMS-101CA CMS-102CA |
| 25-mm overall width | - | CMS-200S8 CMS-201S8 CMS-202S8 | CMS-200DR CMS-201DR CMS-202DR | CMS-200CA CMS-201CA CMS-202CA |

Table 1.1

Open-core sensors

In the open-core sensors cables are directly insert without using a screwdriver, guaranting a faster cabling.

The open-core sensors should be able to measure all types of current, whether AC, DC or mixed, up to 80 A in TRMS, enabling exact and effective measurements.

The open-core senors are available in 18 mm width.

The open-core sensors could be installed in all kind of application, except for all S800 devices with cage terminals.

In the Table 1.2 there are listed the whole range of possible open-core sensors, divided into type of application and mesasurement range:

| Open-core sensors | System pro M, SMISSLINE | S800 | DIN rail | Cable tie |
| --- | --- | --- | --- | --- |
| Measuremnet range | For all LS, FI 6 FI-LS with twin terminals | For all S800 devices with cage terminals | Universally usable | Universally usable |
| 18 mm overall width | 80 A | CMS-120PS | - | CMS-120DR | CMS-120CA |
|  | 40 A | CMS-121PS | - | CMS-121DR | CMS-121CA |
|  | 20 A | CMS-122PS | - | CMS-122DR | CMS-122CA |

Table 1.2

Solid-core sensors

In the solid-core sensors cables are closed inside the core, guaranting a secure insertion.

The solid-core sensors should be able to measure all types of current, whether AC, DC or mixed, up to 160 A in TRMS, enabling exact and effective measurements.

The solid-core senors are available in 18 mm and 25 mm width.

The solid-core sensors could be installed in all kind of application.

In the Table 1.3 there are listed the whole range of possible open-core sensors, divided into type of application and mesasurement range:

| Solid-core sensors | System pro M, SMISSLINE | S800 | DIN rail | Cable tie |
| --- | --- | --- | --- | --- |
| Measuremnet range | For all LS, FI 6 FI-LS with twin terminals | For all S800 devices with cage terminals | Universally usable | Universally usable |
| 18 mm overall width | 80 A | CMS-100PS | CMS-100S8 | CMS-100DR | CMS-100CA |
|  | 40 A | CMS-101PS | CMS-101S8 | CMS-101DR | CMS-101CA |
|  | 20 A | CMS-102PS | CMS-102S8 | CMS-102DR | CMS-102CA |
| 25 mm overall width | 160 A | - | CMS-200S8 | CMS-200DR | CMS-200CA |
|  | 80 A | - | CMS-201S8 | CMS-201DR | CMS-201CA |
|  | 40 A | - | CMS-202S8 | CMS-202DR | CMS-202CA |

Table 1.3

# ACCESSORIES – FLAT CABLE

The control unit of the circuit monitoring system need a flat cable for receive branches measurements from sensors.

The flat cable should be a 4-pin cable, flexible in length.

The maximum flat cable length that could be installed must depend on the number and shape of sensors, as it is shown on the Table 2.1:

| Flat cable | Maximum flat cable length in m |
| --- | --- |
| Number of sensors | Solid-core sensors | Open-core sensors |
| 32 | 4.5 | 7.5 |
| 28 | 5 | 8.5 |
| 24 | 6 | 10 |
| 20 | 7 | 12 |
| 16 | 8.5 | 15 |
| 12 | 11 | 20 |
| 8 | 16 | 30 |
| Length | Flat cable |
| 2 | CMS-800 |
| 5 | CMS-802 |
| 10 | CMS-803 |
| 30 | CMS-805 |

Table 2.1

# ACCESSORIES – OTHER COMPONENTS

External current transformers should be installed in a circuit monitoring system, with a secondary of 5 A.

A connector housing and a connectors should be installed in order to connect the flat cable with the sensors.