
[image: image2.png]



                       SafeGear Medium Voltage Arc-Resistant 

                            Metal-Clad Switchgear Specification
TABLE OF CONTENTS

21.
SCOPE


22.
REFERENCES


33.
GENERAL DESIGN REQUIREMENTS


54.
BASIC CONSTRUCTION


85.
POWER CIRCUIT BREAKERS


106.
INSTRUMENT AND CONTROL POWER TRANSFORMERS


127.
RELAYING


128.
GENERAL CONTROL AND METERING


139.
CONTROL DEVICES AND WIRING


1310.
NAMEPLATES


1411.
FINISH


1412.
TESTING


1513.
ENGINEERING DATA REQUIREMENTS


1714.
PREPARATION FOR SHIPMENT


1715.
SHIPPING


1816.
PROVISIONS FOR HANDLING AND FIELD ERECTION




METAL-CLAD SWITCHGEAR

1. SCOPE

1.1. This Specification covers the basic design and functional requirements for arc-resistant medium voltage metal-clad switchgear with vacuum circuit breakers.  It is provided as a guide to assist in the specification of arc-resistant medium voltage switchgear and is intended as a supplement to single line diagrams and data sheets for switchgear projects.

2. REFERENCES
2.1. The assemblies shall be constructed, wired, and tested in accordance with all applicable sections of the latest listed Standards and Codes.

2.1.1. American National Standards Institute, Inc. IEEE / (ANSI)

2.1.1.1. C37.04 Standard Rating Structure for AC HV Circuit Breakers

2.1.1.2. C37.06 Preferred Ratings for AC HV Circuit Breakers

2.1.1.3. C37.09 Standard Test Procedure for AC HV Circuit Breakers

2.1.1.4. C37.010 Application Guideline for AC HV Circuit Breakers

2.1.1.5. C37.011 Application Guide for TRV for AC HV Circuit Breakers

2.1.1.6. C37.012 Application Guide for Capacitance Switching

2.1.1.7. C37.11 Requirements for Electrical Control

2.1.1.8. C37.20.2 Standard for Metal-Clad and Station-Type Cubicle Switchgear

2.1.1.9. C37.20.7 Testing Guide for Switchgear Internal Arcing Faults 
2.1.1.10. C37.55 Conformance Testing Procedure of Metal-Clad Switchgear

2.1.1.11. C57.10 Requirements for Instrument Transformers 

2.1.1.12. C57.13 Requirements for Instrument Transformers

2.1.1.13. 47 Guide for Surge Withstand Capability Tests


2.1.2. National Electrical Manufacturers Association (NEMA)

2.1.2.1. CC1 Electrical Power Connectors

2.1.2.2. SG-4 Standards for Power Circuit Breakers

2.1.2.3. SG-5 Power Switchgear Assemblies

2.1.3. NEC / NFPA

2.1.3.1. 70E 2002 Edition (applicable portions)

2.2. Design tests, to verify ANSI ratings as identified in this specification, shall be documented as required by ISO9001-2000 and available for review and inspection.

2.3. Optional - Seismic assessment shall be conducted to assure the switchgear will withstand seismic levels through UBC Zone 4. Any special design or installation considerations to assure compliance with this requirement will be thoroughly documented on project drawings.

2.4. It shall be the Vendor and/or manufacturer's responsibility to be, or to become, knowledgeable of the requirements of these Standards and Codes.  Any changes or alternations to the equipment to make it meet Standards and Codes requirements shall be at the expense of the Vendor.

3. GENERAL DESIGN REQUIREMENTS
3.1. The arc-resistant switchgear shall have a voltage rating of (4.76/8.25/15) kV, with (X) main circuit breaker(s), (X) tie circuit breaker(s), (X) feeder breaker(s) (X feeder breakers on each side of the tie.) There will be a total of (X) circuit breakers and (X) sections.  The switchgear will be One/Two high construction with indoor frame size of 36” wide x 95” high x (standard – 85”, optional – 92”) deep.  End dress panels will be provided on each end of a lineup and can extend the width by approximately one inch on each end.  The arc-resistant switchgear shall be designed and manufactured in accordance with ANSI C37.20.2 and shall conform to the rigid construction and design parameters associated with the internal arcing fault testing standards as defined in IEEE C37.20.7. The switchgear will be used in a (X) kV, 3-phase, 60 Hz system. It shall be composed of factory assembled metal clad cubicles. The circuit breakers shall be designed with vacuum interrupter technology and shall incorporate a (spring operated or magnetically actuated) mechanism.

3.2. Ratings

3.2.1. The switchgear will have the following rating:

3.2.1.1. Rated Maximum Voltage

(4.76/8.25/15) kV

3.2.1.2. Operating Voltage


(X) kV

3.2.1.3. Main Bus Continuous Rating
(1200/2000/3000) A



3.2.1.4. Control bus DC Voltage (Nom.)
(48 VDC/125 VDC/250 VDC/120 VAC/240 VAC)

3.2.1.5. Circuit Breaker Interrupting

(25/31.5/40/50) kA

3.2.1.6. Close and Latch


(65/82/104/130) kA Peak

3.2.1.7. Breaker Interrupting Time

3 cycles

3.2.1.8. Temperature rise of the switchgear will be in accordance with the latest revision
                 of ANSI C.37.20 for metal clad switchgear.

3.2.1.9. The equipment shall be completely factory assembled and tested prior to
                 shipment. 

3.2.1.10. The below table provides the required ratings and related capabilities of 
                 circuit  breakers utilized in this switchgear project:

	 

	 

	 

	 

	 

	 

	 

	 


	Nominal

	Rated

	Low Frequency

	Impulse

	Rated

	Short Time

	Close

	Rated


	Voltage

	Maximum

	Withstand

	Level (BIL)

	Short Circuit

	Current

	and

	Voltage


	Class

	Voltage

	Voltage

		Current

	2 Second

	Latch

	Range Factor


	kV

	kV

	kV rms

	kV Crest

	kA rms

	kA rms

	kA Peak

	K


	 

	 

	 

	 

	 

	 

	 

	 


	 

		 

		 

		 

	 


	4.16

	4.76

	19

	60

	31.5

	31.5

	82

	1.0


	 

		 

		 

		 

	 


	4.16

	4.76

	19

	60

	40

	40

	104

	1.0


	 

		 

		 

		 

	 


	4.16

	4.76

	19

	60

	50

	50

	130

	1.0


	 

		 

		 

		 

	 


	7.2

	8.25

	36

	95

	40

	40

	104

	1.0


	 

		 

		 

		 

	 


	13.8

	15

	36

	95

	20

	20

	52

	1.0


	 

		 

		 

		 

	 


	13.8

	15

	36

	95

	25

	25

	65

	1.0


	 

		 

		 

		 

	 


	13.8

	15

	36

	95

	31.5

	31.5

	82

	1.0


	 

		 

		 

		 

	 


	13.8

	15

	36

	95

	40

	40

	104

	1.0


	 

		 

		 

		 

	 


	13.8

	15

	36

	95

	50

	50

	130

	1.0


	 

	 

	 

	 

	 

	 

	 

	 



	


4. BASIC CONSTRUCTION
4.1. The switchgear assembly shall consist of metal‑clad, free‑standing, vertical, dead‑front steel structures containing circuit breaker compartments and circuit breakers, primary bus system, ground bus system, auxiliary compartments and transformers, protection and control devices, control bus (as required) and connection provisions for primary, ground, and control circuits.  The basic structure will be of modular construction and fabricated mainly of highly reflective, 14 gauge galvanic steel, which does not require painting due to superior resistance to corrosion.  The switchgear enclosure will be constructed of double wall galvanic steel with an air gap between sheets and in the event of a fault condition, the first layer will burn and the second layer will be insulated by the air gap. 

4.2. The switchgear system shall be comprised of the following discrete modules, arranged in an overall height of 95” for each vertical section, with the height of each compartment shown in [brackets]:

4.2.1. 1200, 2000, or 3000 amp circuit breaker compartments [38”]

4.2.2. Low voltage instrument compartments [19, 38, or 57”]

4.2.3. Bus and cable compartments [overall height = 95”]

4.2.4. Auxiliary compartments (PT, CPT, Fuse, etc.)

4.2.4.1. Draw-out PTs [19”]

4.2.4.2. Draw-out CPTs or fuses [38”]

4.3. The circuit breaker enclosure shall include stationary support bushings and primary contacts for engagement with the circuit breaker or ground and test (G&T) device. Standard bushings shall be made of glass-reinforced polyester (or optional porcelain) capable of supporting the weight of the current transformers. Primary contacts will be made of copper and designed to accept round, tulip style connectors.

4.4. The switchgear shall be designed so that future units can be added to each end (unless coupled to other equipment). A removable plate will cover any unused openings in the side of the gear.

4.5. Hem-bends (rigid overlap bending) will be consistently used when building the switchgear compartments to enhance strength and to minimize potential exposure of working personnel to sharp steel edges during installation and maintenance.

4.6. A ¼” x 2” tin plated copper ground bus shall be provided for the entire length of the switchgear.  It shall be equipped with a solderless connector for #2/0 AWG copper cable at each end.  The ground bus shall be accessible in the cable compartment, and shall have connection points in each switchgear section for workmen's grounds. The ground bus will be connected to the breaker frames and will ground the draw-out circuit breaker in and when traveling in between the connected and test positions. Bare, un-plated copper ground bus is unacceptable.

4.7. Bus bars

4.7.1. The main bus compartment shall be separated from the other compartments by an 11 gauge steel barrier (or equivalent) and shall fully enclose the main bus.  The main bus compartment will be accessible from the rear through the cable compartment.  Main bus ratings shall match the highest rated circuit breaker continuous current ratings and comply with ANSI / IEEE temperature rise requirements.  

4.7.2. Bus bars shall be copper and shall be completely isolated and fluidized epoxy insulated with flame retardant, non‑hygroscopic, high‑dielectric insulation, except at bolted joints.  The bus shall be mechanically braced for the close and latch rating of the breaker having the highest interrupting rating in each assembly.  All bolted bus joints shall be (Standard – silver-plated) (Optional – tin-plated). The bus connections to the circuit breakers shall match the breaker rating.  Bus supports shall be flame retardant, track resistant GPO-3 glass polyester (Optional – porcelain). 

4.7.2.1. Bus joint covers shall be removable for field inspection and maintenance, and shall be reusable.  Removable insulating boots shall be used on all bolted bus joints. Taping of bus joints is unacceptable.  

4.7.3. The shape of the bus bar shall be full round edge.  The main bus shall not be tapered.

4.7.4. Bus bar connections shall be mechanically secured with reusable fastening devices that shall maintain adequate pressures at the joints within the operating temperature range of the switchgear.

4.7.5. The bus bars and support systems shall be designed to withstand the forces created during short circuit conditions at the rated momentary and short-time (2-second) conditions of the highest rated circuit breaker. Supports shall be made of (Standard - glass polyester) (Optional - porcelain).

4.7.6. A cable termination bus shall be provided from the circuit breaker / switchgear primary disconnects to a cable compartment location to allow cable connections. Bus connections to cables and bus duct shall be rigid.  Cable termination bus arrangement shall allow at least 36 inches for primary cable terminations and stress cones. Connections to roof entrance bushings shall be of the flexible type. 

4.7.7. Standard termination bus shall meet the bolthole requirements of NEMA CC1-4.05, and shall typically be the NEMA 4-hole pattern. (Optional - Vendor will supply - crimp type cable lugs, compression type cable lugs, - as shown on project data sheets.)

4.7.8. The design shall be adaptable for top or bottom primary entrance arrangements. In 2-high arrangements, each set of primary connections and zero-sequence current transformers, if applicable, shall be isolated into separate compartments by a grounded steel partition in accordance with ANSI standards.

4.8. Bar type / zero sequence current transformers, lighting arrestors, surge capacitors, stationary control power transformers, ground sensors, or other auxiliary equipment shall be mounted in the cable compartments as shown on the single line diagram and project data sheets.  An optional 7” rear extension shall be provided to accommodate additional equipment and power cable as needed.

4.9. Control switches, instruments, meters, position indicating lights, protective relays, etc. shall be in a separate compartment from the circuit breaker. Monitoring devices such as CTs and limit switches may be located within other compartments.  Low voltage compartment door mounted devices shall be mounted on the front of the switchgear panels and arranged in an approved, logical, symmetrical manner.

4.10. The breaker cubicles and circuit breaker units shall be constructed so that each unit of the same rating is interchangeable.

4.11. Solidly grounded metal (Optional – non-metallic poly carbonate) shutters shall automatically open when the breaker or G&T device is racked into the connected position and close (covering the primary contacts and current transformers) when racked to the test or disconnected positions or withdrawn from the cell.  Shutter grounding shall be by dedicated ground wires, and shall not be dependent on grounding through hinges or moving contact surfaces.  The actuation of the shutters must be by the movement of the circuit breaker. Gravity and spring-operated shutters are unacceptable.

4.12. Switches

4.12.1. Breaker control switches shall not be mounted adjacent to meter switches, and shall have "pistol grip" handles.  Switches to be Electroswitch Series 24 or equivalent.

4.12.2. Meter switches shall have "knurled knob" handles.  Switches to be Electroswitch Series 24 or equivalent.

4.12.3. Control and instrument switches will be provided and wired in accordance with specified single line diagrams and data sheets, and will be mounted only on low voltage compartment doors and panels.

4.13. Externally‑visible, permanent nameplates shall be provided to identify each instrument, instrument switch, meter, relay, control switch, indicating light, circuit breaker compartment, potential transformer compartment, and auxiliary compartment.  Equipment and terminal blocks within the compartments shall be suitably identified.  Relays shall be designated as to use and as to the phase to which they are connected.  Nameplates shall be laminated plastic.  Characters shall be black letters on a white background.

4.14. Auxiliary switches shall be wired out to terminal blocks for customer convenience.

4.15. The compartment door shall be securely held with tamper-resistant hinges and sealed with (standard - multiple, tamper-resistant, captive manual fasteners) (optional - a single handle, multi-point latching mechanism in available ratings).  (Optional -Compartment doors will include provisions for padlocking. Others to supply locks).

5. POWER CIRCUIT BREAKERS
5.1. The power circuit breakers shall be electrically operated, 3-pole, draw-out type, with electric motor and manual charging of a spring type stored energy operating mechanism.  The power circuit breaker shall be provided with self‑aligning line‑side and load‑side disconnecting devices.  Circuit breakers to be ABB type ADVAC.

OR


The power circuit breakers shall be electrically operated, 3-pole, draw-out type, with magnetic actuator and a capacitor stored energy operating mechanism.  The power circuit breaker shall be provided with self‑aligning line‑side and load‑side disconnecting devices.  Circuit breakers to be ABB type AMVAC. The circuit breaker mechanism shall have a life of 100,000 operations.

5.2. Breaker racking system shall allow smooth, consistent breaker movement with the door closed and shall have three positions in addition to the fully withdrawn position; disconnect, test and connected.  The circuit breaker shall stop and lock in all three positions, requiring operator action to move from one position to another.  The circuit breaker door must be provided with impact resistant poly carbonate viewing window of at least 86 square inches and ½” thick to determine breaker position, open/closed indicator, spring charge status, and operations counter.

5.3. The circuit breaker will be provided with an integral racking mechanism.  Circuit breakers utilizing switchgear mounted racking mechanisms separate from the circuit breaker are unacceptable.  

5.4. The draw-out mechanism shall hold the breakers rigidly in the CONNECTED (primaries and secondaries engaged), TEST (primary contacts disconnected and shutter closed, but control contacts engaged) and DISCONNECTED (both primary and secondary contacts disengaged) positions, with the door closed.  

5.5. The breakers in the upper compartment and lower compartment shall be held captive in the cubicle by means of a latching mechanism, even in the disconnected position. Removal of the circuit breaker shall be by means of unlatching the mechanism and pulling the circuit breaker onto a lift truck.  Cell must have a minimum of a 1” lip for proper sealing of the door and to prevent ingress of dirt and other contaminants.  Circuit breakers that require rail extensions are unacceptable. 

5.6. Wheels shall be provided on the bottom of the circuit breaker for easy floor rolling after the breaker is removed from the frame. Circuit breakers that require a separately purchased floor rolling truck assembly are unacceptable.
5.7. Interlocks shall be provided which will prevent connecting the breaker to, or disconnecting it from the bus stabs unless the breaker is OPEN (tripped), assuring proper sequencing and safe operation.  The close springs of the circuit breaker will automatically discharge when the breaker is released from the cell by pulling in on the truck latch assembly. Provisions shall be made for the addition of optional KIRK KEY interlocks, as shown on project data sheets and the single line diagram.
5.8. Control voltage and trip voltage shall be as follows:

5.8.1. The breaker motor charging range shall be (48VDC/125VDC/250VDC/120VAC/240 VAC). The trip voltage shall be (48VDC/125VDC/250VDC/120VAC/240 VAC).  The close voltage shall be (48VDC/125VDC/250VDC/120VAC/240 VAC).The direct current power source shall be by owner.

5.8.2. Close and trip circuits for each breaker shall be separately fused.  Fuse blocks shall be dead front, pull‑out type, which provide the control power disconnecting means.

5.9. The ADVAC circuit breaker shall be provided with a toroidal spring mechanism, which allows for the easiest manual charging in the industry. The mechanism shall rotate the main horizontal shaft in only one direction, in order to reduce wear and maintenance costs and eliminating mechanism binding.  The breaker shall be equipped with the "stored energy operation" type, anti‑pump-operating mechanism.  It shall be possible to open and close the breakers manually.  The circuit breaker shall be capable of operating in three cycles which means smaller power cables, lower construction costs, and improved system quality.  The mechanism shall be completely front accessible and maintainable by removing the faceplate.  Breakers that require lifting to access the mechanism under the carriage are unacceptable.

Or

The AMVAC circuit breaker shall be provided with a magnetically actuated mechanism which shall use a flux-shifting device with integral permanent magnets. It also shall incorporate an electronic controller and a capacitor for energy storage. The AMVAC circuit breaker mechanism shall be capable of 100,000 operations.  The breaker shall be virtually maintenance free, except for minor lubrication.  The circuit breaker shall be capable of operating in three cycles which means smaller power cables, lower construction costs, and improved system quality.  The mechanism shall be completely front accessible and maintainable by removing the faceplate.  Breakers that require lifting to access the mechanism under the carriage are unacceptable. It shall be possible to program the electronic controller to react in three different ways upon loss of control power: 1) trip the circuit breaker immediately, 2) trip the circuit breaker with a delay, or 3) remain in the closed position.

The AMVAC circuit breaker shall have the capability of accepting AC and DC as control power within the following ranges without changing the electronic board:


16.8 to 75 VDC and 20.4 to 52.8 VAC


OR


77 to 280 VDC and 85 to 264 VAC

5.10. The draw-out mechanism shall hold the breakers rigidly in the CONNECTED (primaries and secondaries engaged), TEST (primary contacts disconnected and shutter closed, but control contacts engaged) and DISCONNECTED (both primary and secondary contacts disengaged) positions, with the door closed. The secondary contact plug shall automatically disconnect when the breaker is moved from the TEST to the DISCONNECTED position. A single (25 pin) fully automatic, self-aligning, secondary disconnecting device shall be provided to act as a disconnect for the secondary connections between the circuit breaker and the switchgear.  The disconnecting device shall be positioned and constructed as to not expose the operator to live parts. The secondary disconnect shall connect automatically when the circuit breaker is racked into the test and connected positions. A double (50 pin) disconnect arrangement shall be available as an option and provided as shown on project data sheets.  The female portion of the disconnect system shall reside in the breaker compartment, so that energized contacts are recessed and remain “touch safe”.  To guarantee the integrity of operating personnel, it shall not be required to open or keep opened the door of the circuit breaker compartment after the breaker has been locked in the disconnected position to be able to rack the breaker or connect the secondary contacts, Circuit breakers that require manual connecting of the secondary contacts are unacceptable.

5.11. The circuit breaker enclosure shall have interference blocking to prevent the insertion of improperly rated breakers. Note: Circuit breakers with single secondary disconnect are not interchangeable with devices using a dual secondary disconnect.

5.12. The breaker shall include 8 on-board auxiliary contacts (4a, 4b), wired through the secondary disconnect. Up to 9 additional contacts (5a, 4b) can be installed on the breaker and wired through the secondary disconnect, for a total of 17 on-board contacts. All breaker-mounted contacts shall operate in both connected and test positions.  Mechanism operated cell switches that are external to the circuit breaker requiring complex linkages external to the breaker are unacceptable. 

5.13. Provisions for padlocking breakers in any of the positions shall be included.

5.14. Circuit breaker power draw-out contacts shall be silver-plated.

5.15. The breaker shall have flags to indicate open or closed position, and spring charge status.  Only the correct status flag for any single function shall be visible.  Additionally, the breaker shall have a 5-digit, non-resettable operations counter.

6. INSTRUMENT AND CONTROL POWER TRANSFORMERS
6.1. Current Transformers

6.1.1. CT nameplates shall be located on the CT housing and information provided shall be in accordance with ANSI C57.13. The CT winding shall terminate on a screw type terminal on the CT housing and shall be wired to shorting terminal blocks. ABB type SAB current transformers shall be supplied as shown on project data sheets and the single line diagram. Zero sequence transformers shall be ABB type BYZ-S.
6.1.2. Each current transformer shall have a 5 ampere secondary and a primary rating as shown on the Data Sheets and One‑Line diagram.
6.1.3. Ratings and accuracies shall be in accordance with ANSI C57.13 for the metering and relay applications shown on the Data Sheets.

6.1.4. Each current transformer shall have a short-circuiting device (shorting type terminal blocks). The first termination of each current transformer shall be at the short-circuiting device terminal blocks where the ground connection is also made.

6.1.5. Low voltage ring core type CT’s will be bushing-mounted, located behind the shutters and accessible from the front. Bushing design will accommodate up to four standard accuracy CT’s per phase (two on the bus side and two on the load side) for all ratings.
6.2. Potential Transformers

6.2.1. Potential transformer shall be designed to withstand the Basic Impulse Level (BIL) of the switchgear. Potential transformers shall always be fused. Potential transformers shall be mounted on a draw-out unit in an auxiliary enclosure, which disconnects them from the primary circuit safely. ABB type VIY and VIZ potential transformers shall be supplied in accordance with project data sheets and the single line diagram.

6.2.2. Potential transformers shall be mounted in a separate draw-out compartment (truck assembly) and so arranged that the unit can be withdrawn from the operating position via a racking device with the door closed.  In the withdrawn position, the fuses shall be completely disconnected from service and all exposed parts shall be visibly grounded.

6.2.3. The potential transformers compartment shall incorporate extension rails to allow changing fuses and general maintenance without the need to take the truck assembly completely out of its compartment.

6.2.4. Potential transformers shall be connected to the line or load via solid copper rod, bus or shielded cable.

6.2.5. An impact resistant glass-viewing window shall be on the front of the potential transformer door.

6.2.6. Each transformer shall be protected with current‑limiting primary fuses, and shall be designed to withstand the basic impulse level of the switchgear.

6.2.7. Each transformer shall have a 120-volt secondary and an ANSI C57.13 accuracy classification meeting the requirements of the application shown on the Data Sheets.

6.3. Control Power Transformers

6.3.1. Control power transformers shall be dry type with disconnecting type current limiting primary fuses and fused 120 volt secondary.  Transformers up to 15kVA single phase (or fuses above 15kVA) shall be mounted on a truck assembly, which is moved between the connected and disconnected position via closed door racking and utilizing the same racking device as the circuit breaker. 

7. RELAYING 
7.1. All protective relays, auxiliary relays, indicating instruments, recording instruments, indicating lights, transducers, etc. shall be housed in the low voltage compartment unless specifically allowed by the project data sheets.  The low voltage compartment shall isolate the above equipment so that additional arc flash protection is available. Relays and instruments shall be provided and wired as specified on the project single line diagram and data sheets. A multi-function, 3-phase microprocessor based relay and control package shall be used in 2-high arrangements. Alternative relay types may be used in 1-high configurations to the extent allowed by mounting space in the low voltage compartments. Door-mounted protective relays will be draw-out type whenever practical.

7.2. Protective relays and test devices shall be semi-flush mounted.  The relays shall be so arranged that they can be tested in position on the panel and readily withdrawn from the panel for inspection or replacement.

7.3. The relays shall be provided with targets with an external reset feature.
7.4. Switchgear device function numbers shall be in accordance with ANSI Standard C37.20.

7.5. An ABB DPU200R distribution protection relay or equivalent shall be provided with the following functions:

7.5.1. 3-phase overcurrent protection (time and instantaneous)

7.5.2. Ground overcurrent (time and instantaneous)

7.5.3. Multi-shot reclosing

7.5.4. High set instantaneous

7.5.5. Ammeter, demand and peak demand ammeters

7.5.6. Event recording

7.5.7. Accumulation of breaker interrupting duty 

7.5.8. Continuous self-checking

7.5.9. RS-232 and RS-485 communications ports for remote terminal connection.

8. GENERAL CONTROL AND METERING
8.1. Instruments and meters shall be rectangular and anti-fungi, black finish, dust proof and semi-flush mounted digital switchboard type. 

8.2. Meter potential coils shall be 115 volts and current coils shall be five (5) amperes.

8.3. The equipment panel shall be arranged symmetrically and when possible shall allow for possible future additions.

8.4. Instrument switches shall have black knurled non-removable handles. The circuit breaker controls shall have non-removable pistol grip handles.

9. CONTROL DEVICES AND WIRING
9.1. Control devices, control buses, local control, instrument cables and wiring on the equipment shall be installed at the factory.  Low voltage cables shall be enclosed in grounded metal flexible conduit when routed through a high voltage compartment.  Control wiring shall be neatly bundled and tie wrapped where applicable. Wiring shall be protected from rubbing against door flanges or other parts of the enclosure.

9.2. Control relays, auxiliary contacts and small mechanisms shall be enclosed, protected and accessible for maintenance.

9.3. Fuses shall be provided in each closing circuit of each circuit breaker. These fuses shall be respectively located in the low voltage compartment of the circuit breaker frame. Only the closing circuit shall be fused; there shall be no fuses in the tripping circuit.
9.4. Control wire shall be fourteen (14) gauge SIS stranded, extra-flexible, 600V flame retardant, gray color and UL-listed wire except where larger sizes are needed for current carrying requirements.  Current transformers shall be provided with a minimum of twelve (12) gauge.  The conductors shall be stranded copper for fixed wiring and extra flexible stranded copper for hinge wiring.  The conductors shall be 90 degrees Celsius normal operating temperature, flameproof 600-volt switchboard cable and shall meet ICEA S-66-524 NEMA publication No. WC-7 Standards for cross-linked thermosetting polyethylene insulated wire and cable. Flexible connections between stationary and hinged panels or doors shall be made between terminal blocks or clamped in such a manner as to afford flexibility without damage to the wires.  The wires shall be neatly bundled and tie wrapped.

9.5. The assembled control equipment and wiring connections shall be insulated for 600-volts and shall be subjected to a one (1) minute test of 1500-volts AC at the factory after fabrication and assembly is complete.

9.6. Terminal blocks shall be provided for terminating all power and control wiring. Terminal blocks shall be rated at 600-volts, strap screw terminals with white marking strips showing terminal numbers.

9.7. Terminal blocks shall be conveniently located for external connection without accessing the high voltage compartments and shall be marked appropriately. A wire label at both ends will identify each internal connecting wire. (Optional - Marked wires or wire markers shall be provided on both ends of every conductor.)

10. NAMEPLATES
10.1. Nameplates shall be laminated white plastic with black lettering.

10.2. Nameplates shall be provided on all relaying, metering, and control devices.

10.3. Circuit identification nameplates shall be placed on the front and back of each switchgear frame.

11. FINISH
11.1. All non-galvanic steel within the switchgear and metal‑enclosed bus enclosures shall be cleaned, iron phosphated and painted in accordance with the manufacturer's standard practice for the environmental conditions specified.  The enclosure final exterior color paint coat shall be ANSI No. 61 gray.

11.2. The interior shall utilize galvanic steel for internal construction. The galvanic steel shall provide inherent reflective properties to its surface and shall not peal, scratch, rust or corrode.  Painted interiors are subject to scratching during racking of the circuit breakers and normal maintenance of the switchgear and are therefore unacceptable. 

11.3. Manufacturer shall supply paint, matching each color used, for field "touch up" after installation of the equipment.


12. TESTING


12.1. The control circuits shall be operated at the normal voltage and current for proper operation of circuit breakers, circuit breaker simulators, switches, contactors, interlocks, etc.


12.2. Instruments shall be energized from the low voltage winding of the potential transformers and the low current winding of current transformers.  Where practical, each instrument shall be operated through its range of voltage, current and/or phase angle and frequency to produce deflections over the entire scale.


12.3. The ratio and interconnections of all potential transformers shall be functionally checked to verify conformance to the electrical drawings and electrical bills of material.


12.4. Relays shall be tested by applying rated current and/or voltage as required to determine proper performance characteristics.  Each relay shall be tested to determine its proper operation in itself and also in the total overall circuit performance.


12.5. A static circuit check shall be performed for auxiliary switches, external circuit connections and parts of circuitry that have not been checked or cannot be checked functionally.  The devices shall be checked for mechanical function and for conformance to the schematic and wiring diagrams.


12.6. After all electrical tests and mechanical checks have been completed and corrections have been signed off, the following dielectric tests shall be performed:


12.6.1. Each power bus shall be given a high voltage withstand test from phase to phase and phase to ground at the specified voltage, frequency and time duration indicated in the Standard C37.20.


12.6.2. Control wire shall be given a high voltage withstand test from wire to ground at the specified voltage, frequency and time duration with reference to the proper standard.

13. ENGINEERING DATA REQUIREMENTS
13.1. All engineering data provided for the equipment shall show equipment as specified and ordered.  Engineering data, as listed below, shall be supplied in the quantities shown on the supplier’s quotation.

13.2. Standard Class I drawings shall consist of a system single line drawing; front view; floor plan and section view drawing.  Standard Class II drawings shall consist of Class I drawings plus 3-phase elementary and schematic diagrams, nameplate drawing, instrument layout and bills of material. 

13.3. Drawings shall indicate all equipment, but only such equipment, as is actually in the switchgear scope of supply. All user connection and interface points shall be clearly marked, including primary and secondary cable entrances and connection points, installation details, generic interframe assembly and generic connection details for shipping splits.

13.4. Drawing Requirements

13.4.1. AutoCad Version 2000 or greater supplied for all drawings.

13.4.2. Electronic drawing PDF format files for approval shall be supplied. Where possible, typical drawings shall be supplied as PDF files for class 1 and either PDF files or AutoCAD files for class 2.
13.4.2.1. Structural Drawings, with critical dimensions, showing:

13.4.2.1.1. Arrangement.

13.4.2.1.2. Plan, front view, and elevation section views.

13.4.2.1.3. Required clearances for opening doors and for removing breakers.

13.4.2.1.4. Conduit or cable trays entrance locations and dimensions for both top and bottom entrance.

13.4.2.1.5. Bus bar locations and configurations.

13.4.2.1.6. Incoming and outgoing power cable terminator positions.

13.4.2.1.7. Anchor bolt locations.

13.4.2.1.8. Grounding connections.

13.4.2.1.9. Weight of equipment.

13.4.2.1.10. Plenum detail when required.

13.4.2.2. Elementary Three Line Diagrams

13.4.2.2.1. Three line diagrams, with ANSI device function numbers used throughout, shall show all:

13.4.2.2.1.1. Instrument transformers.

13.4.2.2.1.2. Relays.

13.4.2.2.1.3. Meters and meter switches.

13.4.2.2.1.4. Breakers and other pertinent devices.

13.4.2.3. Schematic Diagrams

13.4.2.3.1. Schematic diagrams shall be furnished for the electrically‑operated breaker / relay control scheme.

13.4.2.3.2. Each schematic diagram shall show all control devices and device contact, each of which shall be labeled with its proper ANSI device function number.

13.4.2.3.3. Each schematic diagram shall show device and terminal block terminal numbers for customer connections.

13.4.2.3.4. Provide control switch development tables.

13.4.2.4. Detailed Connection (Wiring) Diagrams showing, submitted for record only:

13.4.2.4.1. Approximate physical location of all items in each unit.

13.4.2.4.2. All wiring within each unit.

13.4.2.4.3. All interconnecting wiring between units.

13.4.2.4.4. Identification of all terminals, terminal blocks, and wires.

13.4.2.5. Provide one set of drawings shipped with the switchgear for start-up use.

13.5. Material List

13.5.1. An electrical bill of material list shall be furnished listing the quantity, rating, type, and manufacturer's catalog number of all equipment on each unit.

13.6. Installation, Operating, and Maintenance Instructions

13.6.1. Installation, operating, and maintenance instructions shall cover switchgear, breakers, relays, meters and devices requiring installation, programming and / or maintenance.
13.6.2. The breaker operating mechanism shall be front-accessible, and all routine maintenance shall be performed with the breaker in an upright position. The interrupters shall be completely sealed requiring no interphase barriers.  Breakers shall be designed for easy insertion, removal and transport on flat indoor surfaces. A breaker lift truck shall be furnished with each switchgear assembly.
14. PREPARATION FOR SHIPMENT
14.1. Preparation for Shipment shall be in accordance with manufacturer's standards, unless otherwise noted on the Request for Quotation and/or Purchase Order.  The manufacturer shall be solely responsible for the adequacy of the Preparation for Shipment provision employed in respect of materials and application, to provide materials and their destination in ex‑works condition when handled by commercial carrier systems.

15. SHIPPING
15.1. Instructions for receiving, handling, and storage shall be provided.

15.2. Circuit breakers shall not be shipped inside the switchgear assembly to avoid damage.

15.3. Each "shipping section" of stationary structures shall be provided with a permanently‑attached, readily‑visible identification tag bearing the equipment number of the assembly of which it is a part.

15.4. The switchgear shall be split in the most efficient manner for shipping.
15.5. If shipped in sections the wiring between the units shall be terminated on terminal blocks on each side of the shipping split. Jumpers shall be provided and marked for convenient connection in the field.

15.6. All accessory items shall be shipped with the switchgear. Boxes and crates containing accessories shall be clearly marked with the contents.

15.6.1. Accessories include:

15.6.1.1. A breaker lifting truck device to allow a circuit breaker, or auxiliary draw-out unit   [ CPT or fuse] to be elevated and then inserted or withdrawn from upper or lower compartments.

15.6.1.2. Circuit breaker accessories, including a hand crank for manually operating the breaker, PT/CPT/draw-out fuse racking system and/or a handle for manually charging the stored energy system on circuit breakers.

15.6.1.3. An electrical test jumper for connecting the breaker to the switchgear control circuit while the breaker is completely out of the cell.

15.6.1.4. Optional - An electrical test cabinet with door-mounted open and close pushbuttons for testing the circuit breaker away from the switchgear.
15.6.1.5. Optional - Vendor’s standard, manually operated Ground & Test device – 3-terminal or 6-terminal.
15.6.1.6. Optional - Relay/test plug for each type of device, as applicable.
16. PROVISIONS FOR HANDLING AND FIELD ERECTION
16.1. Each shop order shall be furnished with one set of shipping base extensions suitable for crane hooks or slings.
16.2. Each shop order shall also be furnished with removable steel shipping bases that permit the use of pipe rollers or dollies without damaging the frame steel of the equipment.
[image: image1.png]



PAGE  
1
SafeGear MV Metal-Clad Switchgear Specification – 1VAL108002-SS Rev. E April 2008

