## report
Cert. No.
Test Report |  |  |  |  | M-file ref.:
[5 empty] | Date of Issue | 15/03/2010
Customer: |  |  |  |  | Type: | M2AA 112 M 6
Serial no.:
Customer ref.: |  |  |  |  | Order no.:
Rating: |  | Product Code |  | 3GAA113101-_SE
3~Motor IE1
|  | V |  | Hz | kW | r/min | A | cos j | IA/IN | TE[s]
Insul.cl.F |  | 230 | D | 50 | 2.2 | 960 | 10 | 0.66
S1 |  | 400 | Y | 50 | 2.2 | 960 | 5.8 | 0.66
IP55 |  | 415 | Y | 50 | 2.2 | 960 | 5.9 | 0.63
28
Resistance |  |  |  |  | Insulation resistance |  |  | Overload test
Line | Pole |  | Ambient 20 ºC |  | R > 140 Mohm
| 6 | 4.255 | W
High-voltage test
[5 empty] | 2000 | 60 s
Test |  | Line |  |  | Input |  | Output
| Torque [Nm] | U[V] |  | f[Hz] | I[A] | P1 [kW] | P2 [kW] | n[r/min] | cos j | h [%]
No Load |  | 400 | Y | 50 | 3.9 | 0.24 |  | 1000
Rated load (cold) | 21.977 | 400 | Y | 50 | 5.6 | 2.64 | 2.2 | 956
Rated load (stab.) | 21.9311 | 400 | Y | 50 | 5.8 | 2.66 | 2.2 | 958 | 0.66 | 82.8
145% rated load | 33.0022 | 400 | Y | 50 | 7.6 | 4 | 3.2 | 926 | 0.75 | 80.2
Shortcircuit | 17 | 231 | Y | 50 | 16.5 |  |  | 0 | 0.58
Temperature rise at amb.temp. 24 °C |  |  | Temperature |  |  |  |  | Measurement method
Stator winding Pole | (K) | Method |  |  | Pole | ºC | Method | 1 Resistance
6 | 54 | 1 | Ambient |  | 6 | 24 | 3 | 2 Thermometer
|  |  | Frame |  | 6 | 51 | 3 | 3 Thermocouples
Manufactured and tested in accordance with rules of IEC 34-2-1.
On behalf of customer
On behalf of manufacturer |  | Date of test |  |  | 2008-09-19
Tested by Asea Brown Boveri, S.A. /Sabadell
Computer print-out valid without signature
Asea Brown Boveri, S.A
Division Motors
Postal address: | Apdo. de Correos, 81 |  |  |  | Telephone |  |  |  | Telefax
| 08200 SABADELL (SPAIN) |  |  |  | + 34 - 3 - 728 85 00 |  |  |  | + 34 - 3 - 728 85 33