ABB Automation

Effective 5/27/09

Sample Specification for

Variable Frequency Drives

For Centrifugal Pump & Fan Applications

# PART 1-GENERAL

# DESCRIPTION

- This specification is to cover a complete Variable Frequency motor Drive (VFD)	 consisting of a pulse width modulated (PWM) inverter designed for use with a standard NEMA Design B induction motor.

- The drive manufacturer shall supply the drive and all necessary options as herein specified.  The manufacturer shall have been engaged in the production of this type of equipment for a minimum of twenty years. VFD’s that are manufactured by a third party and “brand labeled” shall not be acceptable.  All VFDs installed on this project shall be from the same manufacturer.

## QUALITY ASSURANCE

- Referenced Standards:

- Institute of Electrical and Electronic Engineers (IEEE)

- Standard 519-1992, IEEE Guide for Harmonic Content and Control.

- Underwriters laboratories

- UL508C

- National Electrical Manufacturer’s Association (NEMA)

- ICS 7.0, AC Adjustable Speed Drives

- IEC 16800 Parts 1 and 2

- National Electric Code (NEC)

- NEC 430.120, Adjustable-Speed Drive Systems

- International Building Code (IBC)

a)	IBC 2006 Seismic – referencing ASC 7-05 and ICC AC-156

- Qualifications:

- VFDs and options shall be UL listed as a complete assembly.  VFD’s that require the customer to supply external fuses for the VFD to be UL listed are not acceptable.  VFDs with red label UL stickers, requiring additional branch circuit protection are not acceptable.  The base VFD shall be UL listed for 100 KAIC without the need for input fuses.

- CE Mark – The VFD shall conform to the European Union Electro Magnetic Compatibility directive, a requirement for CE marking.  The VFD shall meet product standard EN 61800-3 for the First Environment restricted level.

3.	The entire VFD enclosure shall be seismically certified and labeled as such in accordance with the 2006 International Building Code (IBC):

- VFD manufacturer shall provide Seismic Certification and Installation requirements at time of submittal.

- Seismic importance factor of 1.5 rating is required, and shall be based upon actual shake test data as defined by ICC AC-156.

- Seismic ratings based upon calculations alone are not acceptable. Certification of Seismic rating must be based on testing done in all three axis of motion.

4.	Acceptable Manufactures

- ABB ACS550 Series.

- Alternate manufacturer’s requests must be submitted in writing to the Engineer for approval at least 20 working days prior to bid.  Approval does not relieve the supplier of specification requirements.

5.	The VFD manufacturer shall have available a comprehensive, Drive Computer Based Training (CBT) product.  The CBT product shall include detailed, interactive sections covering VFD unpacking, proper mechanical and electrical installation, and programming.  The CBT product shall allow the user to provide just-in-time training to new personnel or refresher training for maintenance and repair personnel on the user’s site.  The CBT product shall be repeatable, precise and shall include record keeping capability.  The CBT product shall record answers to simulations and tests by student ID number.  The CBT product must be professionally produced and have interactive sections, student tests, and include video clips of proper wiring and installation.

# 1.03	SUBMITTALS

- Submittals shall include the following information:

- Outline dimensions, conduit entry locations and weight.

- Customer connection and power wiring diagrams.

- Complete technical product description include a complete list of options provided.  Any portions of this specification not met must be clearly indicated or the supplier and contractor shall be liable to provide all additional components required to meet this specification.

- Compliance to IEEE 519 – harmonic analysis for particular jobsite including total harmonic voltage distortion and total harmonic current distortion (TDD).

- The VFD manufacturer shall provide calculations; specific to this installation, showing total harmonic voltage distortion is less than 5%.  Input filters shall be sized and provided as required by the VFD manufacturer to ensure compliance with IEEE standard 519.  All VFD’s shall include a minimum of 5% impedance reactors, no exceptions.

PART 2 – PRODUCTS

2.01 	VARIABLE FREQUENCY DRIVES

- The VFD package as specified herein shall be enclosed in a UL Listed Type enclosure, exceeding NEMA enclosure design criteria (enclosures with only NEMA ratings are not acceptable), completely assembled and tested by the manufacturer in an ISO9001 facility.  The VFD tolerated voltage window shall allow the VFD to operate from a line of +30% nominal, and -35% nominal voltage as a minimum.

- Environmental operating conditions: VFDs shall be capable of continuous operation at 0 to 500 C (32 to 1220 F) ambient temperature as per VFD manufacturers documented/submittal data or VFD must be oversized to meet these temperature requirements.   Not acceptable are VFD’s that can only operate at 40( C intermittently (average during a 24 hour period) and therefore must be oversized.  Altitude 0 to 3300 feet above sea level, less than 95% humidity, non-condensing.  All circuit boards shall have conformal coating.

- Enclosure shall be rated UL Type 1 and shall be UL listed as a plenum rated VFD. VFD’s without these ratings are not acceptable.  NEMA only type 1 enclosures are not acceptable (must be UL Type 1).

B.	All VFDs shall have the following standard features:

- All VFDs shall have the same customer interface, including digital display, and keypad, regardless of horsepower rating.  The keypad shall be removable, capable of remote mounting and allow for uploading and downloading of parameter settings as an aid for start-up of multiple VFDs.

- The keypad shall include Local and Remote selections and manual speed control.  The drive shall incorporate “bumpless transfer” of speed reference when switching between Local and Remote modes.  There shall be fault reset and “Help” buttons on the keypad.  The Help button shall include “on-line” assistance for programming and troubleshooting.

- There shall be a built-in time clock in the VFD keypad.  The clock shall have a battery back up with 10 years minimum life span.  The clock shall be used to date and time stamp faults and record operating parameters at the time of fault.  If the battery fails, the VFD shall automatically revert to hours of operation since initial power up.  Capacitor back-up is not acceptable.  The clock shall also be programmable to control start/stop functions, constant speeds, PID parameter sets and output Form-C relays.  The VFD shall have a digital input that allows an override to the time clock (when in the off mode) for a programmable time frame.  There shall be four (4) separate, independent timer functions that have both weekday and weekend settings.

- The VFD’s shall utilize pre-programmed application macro’s specifically designed to facilitate start-up.  The Application Macros shall provide one command to reprogram all parameters and customer interfaces for a particular application to reduce programming time.  The VFD shall have two user macros to allow the end-user to create and save custom settings.

- The VFD shall have cooling fans that are designed for easy replacement.  The fans shall be designed for replacement without requiring removing the VFD from the wall or removal of circuit boards.  The VFD cooling fans shall operate only when required.  To extend the fan and bearing operating life, the VFD shall cycle the cooling fans on and off as required.

- The VFD shall be capable of starting into a coasting load (forward or reverse) up to full speed and accelerate or decelerate to set point without tripping or component damage (flying start).

- The VFD shall have the ability to automatically restart after an over-current, over-voltage, under-voltage, or loss of input signal protective trip.  The number of restart attempts, trial time, and time between attempts shall be programmable.

- The overload rating of the drive shall be 110% of its normal duty current rating for 1 minute every 10 minutes, 130% overload for 2 seconds.  The minimum FLA rating shall meet or exceed the values in the NEC/UL table 430.250 for 4-pole motors.

- The VFD shall have internal 5% equivalent impedance to reduce the harmonics to the power line and to add protection from AC line transients.  The 5% impedance may be from dual (positive and negative DC bus) reactors, or 5% AC line reactors.  VFD’s with only one DC reactor shall add an AC line reactor.

- The input current rating of the VFD shall be no more than 3% greater than the output current rating.  VFD’s with higher input current ratings require the upstream wiring, protection devices, and source transformers to be oversized per NEC 430.120.  Input and output current ratings must be shown on the VFD nameplate.

- The VFD shall include a coordinated AC transient surge protection system consisting of 4-120 joule rated MOV’s (phase to phase and phase to ground), a capacitor clamp, and 5% impedance reactors.

- The VFD shall provide a programmable loss-of-load (broken belt / broken coupling) Form-C relay output.  The drive shall be programmable to signal the loss-of-load condition via a keypad warning, Form-C relay output, and / or over the serial communications bus.  The loss-of-load condition sensing algorithm shall include a programmable time delay that will allow for motor acceleration from zero speed without signaling a false loss-of-load condition.

- The VFD shall have user programmable underload and overload curve functions to allow user defined indications of broken belt or mechanical failure / jam condition causing motor overload

- If the input reference (4-20mA or 2-10V) is lost, the VFD shall give the user the option of either (1) stopping and displaying a fault, (2) running at a programmable preset speed, (3) hold the VFD speed based on the last good reference received, or (4) cause a warning to be issued, as selected by the user.  The drive shall be programmable to signal this condition via a keypad warning, Form-C relay output and / or over the serial communication bus.

- The VFD shall have programmable “Sleep” and “Wake up” functions to allow the drive to be started and stopped from the level of a process feedback signal.

- The VFD shall have the ability to program local currency and provide display of energy saved as well as tons of CO2 reduced.

- All VFDs to have the following adjustments:

- Three (3) programmable critical frequency lockout ranges to prevent the VFD from operating the load continuously at an unstable speed.  The lockout range must be fully adjustable, from 0 to full speed.

- Two (2) PID Set point controllers shall be standard in the drive, allowing pressure or flow signals to be connected to the VFD, using the microprocessor in the VFD for the closed-loop control.  The VFD shall have 250 ma of 24 VDC auxiliary power and be capable of loop powering a transmitter supplied by others.  The PID set point shall be adjustable from the VFD keypad, analog inputs, or over the communications bus.  There shall be two independent parameter sets for the PID controller and the capability to switch between the parameter sets via a digital input, serial communications or from the keypad.  The independent parameter sets are typically used for night setback, switching between summer and winter set points, etc.

- There shall be an independent, second PID loop that can utilize the second analog input and modulate one of the analog outputs to maintain the set point of an independent process (ie. valves, dampers, etc.).  All set points, process variables, etc. to be accessible from the serial communication network.

- Two (2) programmable analog inputs shall accept current or voltage signals.

- Two (2) programmable analog outputs (0-20ma or 4-20 ma).  The outputs may be programmed to output proportional to Frequency, Motor Speed, Output Voltage, Output Current, Motor Torque, Motor Power (kW), DC Bus voltage, Active Reference, Active Feedback, and other data.

- Six (6) programmable digital inputs for maximum flexibility in interfacing with external devices.  All digital inputs shall be programmable to initiate upon an application or removal of 24VDC or 24VAC.

- Three (3) programmable, digital Form-C relay outputs.  The relay outputs shall include programmable on and off delay times and adjustable hysteresis.  The relays shall be rated for maximum switching current 8 amps at 24 VDC and 0.4 A at 250 VAC; Maximum voltage 300 VDC and 250 VAC; continuous current rating of 2 amps RMS.  Outputs shall be true Form-C type contacts; open collector outputs are not acceptable.

- Run permissive circuit - There shall be a run permissive circuit for damper or valve control.  Regardless of the source of a run command (keypad, input contact closure, time-clock control, or serial communications), the VFD shall provide a dry contact closure that will signal the damper to open (VFD motor does not operate).  When the damper is fully open, a normally open dry contact (end-switch) shall close.  The closed end-switch is wired to a VFD digital input and allows VFD motor operation.  Two separate safety interlock inputs shall be provided.  When either safety is opened, the motor shall be commanded to coast to stop and the damper shall be commanded to close.  The keypad shall display “start enable 1 (or 2) missing”.  The safety input status shall also be transmitted over the serial communications bus.

- The VFD control shall include a programmable time delay for VFD start and a keypad indication that this time delay is active.  A Form C relay output provides a contact closure to signal a plenum damper is open.  This will allow the damper to be driven open before the motor operates.  The time delay shall be field programmable from 0 – 120 seconds.  Start delay shall be active regardless of the start command source (keypad command, input contact closure, time-clock control, or serial communications), and when switching from drive to bypass.

- Seven (7) programmable preset speeds.

- Two independently adjustable accel and decel ramps with 1 – 1800 seconds adjustable time ramps.

- The VFD shall include a motor flux optimization circuit that will automatically reduce applied motor voltage to the motor to optimize energy consumption and reduce audible motor noise.  The VFD shall have selectable software for optimization of motor noise, energy consumption, and motor speed control.

- The VFD shall include a carrier frequency control circuit that reduces the carrier frequency based on actual VFD temperature that allows higher carrier frequency settings without derating the VFD.

- The VFD shall include password protection against parameter changes.

- The Keypad shall include a backlit LCD display.  The display shall be in complete English words for programming and fault diagnostics (alpha-numeric codes are not acceptable).  All VFD faults shall be displayed in English words.  The keypad shall include a minimum of 14 assistants including:

- Start-up assistant

- Parameter assistants

a.	PID assistant

b.	Reference assistant

c.	I/O assistant

d.	Serial communications assistant

e.	Option module assistant

f.	Panel display assistant

g.	Low noise set-up assistant

- Maintenance assistant

- Troubleshooting assistant

- Drive optimizer assistants

- All applicable operating values shall be capable of being displayed in engineering (user) units.  A minimum of three operating values from the list below shall be capable of being displayed at all times.   The display shall be in complete English words (alpha-numeric codes are not acceptable):

Output Frequency

Motor Speed (RPM, %, or Engineering units)

Motor Current

Motor Torque

Motor Power (kW)

DC Bus Voltage

Output Voltage

- Serial Communications

- The VFD shall have an EIA-485 port as standard.  The standard protocols shall be Modbus, [Optional protocols for Profibus, EtherNet, and DeviceNet shall be available.]  Each individual drive shall have the protocol in the base VFD.  The use of third party gateways and multiplexers is not acceptable.

- Serial communication capabilities shall include, but not be limited to; run-stop control, speed set adjustment, proportional/integral/derivative PID control adjustments, current limit, accel/decel time adjustments, and lock and unlock the keypad.  The drive shall have the capability of allowing the DDC to monitor feedback such as process variable feedback, output speed / frequency, current (in amps), % torque, power (kW), kilowatt hours (resettable), operating hours (resettable), and drive temperature.  The DDC shall also be capable of monitoring the VFD relay output status, digital input status, and all analog input and analog output values.  All diagnostic warning and fault information shall be transmitted over the serial communications bus.  Remote VFD fault reset shall be possible.

- The VFD shall include an independent PID loop for customer use.  The independent PID loop may be used for cooling tower bypass value control, chilled water value / hot water valve control, etc.  Both the VFD PID control loop and the independent PID control loop shall continue functioning even if the serial communications connection is lost.  As default, the VFD shall keep the last good set point command and last good DO & AO commands in memory in the event the serial communications connection is lost and continue controlling the process.

- EMI / RFI filters.  All VFD’s shall include EMI/RFI filters.  The onboard filters shall allow the VFD assembly to be CE Marked and the VFD shall meet product standard EN 61800-3 for the First Environment restricted level with up to 100 feet of motor cable.  No Exceptions.  Certified test reports shall be provided with the submittals confirming compliance to EN 61800-3, First Environment.

- All VFD’s through 75HP at 480 V shall be protected from input and output power mis-wiring.  The VFD shall sense this condition and display an alarm on the keypad.  The VFD shall not sustain damage from this power mis-wiring condition.

- OPTIONAL FEATURES – Optional features to be furnished by the drive manufacturer.  All optional features shall be UL Listed as a complete assembly and carry a UL508 label. The VFD with bypass and/or disconnect means enclosure door must be interlocked such that input power is turned off before the enclosure can be opened. The VFD with bypass and/or disconnect means as a package shall have a UL listed short circuit rating of 100,000 amps and shall be indicated on the UL data label.

- The following shall be provided where bypass is required:

1.	A complete factory wired and tested bypass system consisting of output and bypass contactors, a motor overload relay, a control power transformer with primary and secondary fusing, a cover mounted DRIVE-OFF-BYPASS selector switch, a service (isolation) switch and fast acting, current limiting VFD input fuses are required.  Bypass designs, which have no VFD only fuses, or that incorporate fuses common to both the VFD and the bypass will not be accepted

2.	An input circuit breaker with a door mounted external operating handle, interlocked with the enclosure door and lockable in the OFF position with up to three padlocks, to disconnect all input power from the drive and all internally mounted options.

3.	Motor overload protection for the bypass mode is to be provided by a motor overload relay connected in both the drive and bypass modes of operation.  The motor overload relay shall be an adjustable trip, bimetallic overload relay with a class 20 trip characteristic.

4.	The drive output contactor and the bypass contactor are to be electrically interlocked to prevent simultaneous operation.

5.	The bypass system shall NOT depend on the VFD for bypass operation.  The bypass shall be completely functional even if the VFD has been removed from the enclosure for repair / replacement.

- VFD with Bypass and/or Disconnect Means enclosures shall be UL Type/NEMA 1, UL Type/NEMA 12 or UL Type/NEMA 3R.  UL Type/NEMA 3R enclosures are to include a 100 watt, thermostatically controlled space heater and thermostatic control of the force ventilated cooling system.

# PART 3 – EXECUTION

  - INSTALLATION

A.  	Installation shall be the responsibility of the mechanical contractor.  The contractor shall install the drive in accordance with the recommendations of the VFD manufacturer as outlined in the VFD installation manual.

B.  	Power wiring shall be completed by the electrical contractor, to NEC code 430.122 wiring requirements based on the VFD input current.  Caution: VFDs supplied without internal reactors have substantially higher input current ratings, which may require larger input power wiring and branch circuit protection.  The contractor shall complete all wiring in accordance with the recommendations of the VFD manufacturer as outlined in the installation manual.

  - START-UP

- Certified factory start-up shall be provided for each drive by a factory authorized service center.  A certified start-up form shall be filled out for each drive with a copy provided to the owner, and a copy kept on file at the manufacturer.

  - PRODUCT SUPPORT

- Factory trained application engineering and service personnel that are thoroughly familiar with the VFD products offered shall be locally available at both the specifying and installation locations.  A toll free 24/365 technical support line shall be available.

- A computer based training CD or 8-hour professionally generated video (VCR format) shall be provided to the owner at the time of project closeout.  The training shall include installation, programming and operation of the VFD, bypass and serial communication.

3.04 		WARRANTY

A.	The VFD Product Warranty shall be 24 months from the date of certified start-up, not to exceed 30 months from the date of shipment.  The warranty shall include all parts, labor, travel time and expenses.  A toll free 24/365 technical support line shall be available.