# EMC Plan for CE-marked products

This is a form for making an EMC plan where the user and the manufacturer analyze the installation and define the measures to be taken to achieve electromagnetic compatibility. The plan defines the responsibilities of the manufacturer, the installer and the user of the drive. All these parties establish the plan jointly. Fill in and answer the questions below.

| Step 1: Name the parties |
| --- |
| Manufacturer/supplier | ABB Oy, |
| End user | ABC Steel Ab, Stockholm, Sweden |
| Order no. | 111222333 |
| Type of facility (e.g. chemical factory, paper machine) | Steel factory, Building B2, Installation MP14 |
| Application (e.g. pump. fan, conveyor) | Mixer |

| Step 2: Collect power distribution and earthing data |
| --- |
| Power Distribution | Point of coupling: identification code for distribution panel, switchgear or transformer Transformer T14 |
|  | Type of distribution system | TN-C TN-S TT IT |
| Earth Bus | How and where bonded? At supply transformer T14 |

| Step 3: Collect EMC data (High frequency range, only) |
| --- |
| RFI Sensitive Equipment in the Facility | Any equipment in the building or near installation location sensitive to RF disturbances (e.g. process control and measurement, data buses, computers, remote control, etc.)? Describe. | Yes No Fluid measuring system |
|  | Approximate distance from PDS and cabling of PDS | 10…metres |
|  | Most likely coupling path for disturbance | Conducted Radiated |
| RFI Sensitive Equipment Outside the Facility | Any broadcast or communications receiver antennas visible or near the facility (e.g. radar, radio/TV broadcast, amateur, microwave or other)? Describe. | Yes No |
|  | Frequency | … Hz |
|  | Distances from the antenna | … metres |

| Step 4: Define the installation rules |
| --- |
| Follow the installation rules given in the hardware manual of the drive. Assess the following items and describe the solutions. |
| EMC Effectiveness | Items to Be Considered |
| Cabling | - Install the motor cable and other cables separately with a distance of 50cm - Install the supply cable of the drive to different corner of the cable tray than other power cables -Earth cable trays to grounding system of the building. |
| Dedicated Transformer | - Select supply transformer T14 to be supplied with electrostatic shield between primary and secondary windings. |

Signature(s) by person(s) responsible for EMC

Date		2002-01-29

Signature(s)

PDM code: