| Date | Transformer Manufacturer | P.O. | Job No. | Number of Units | Final Customer |
| --- | --- | --- | --- | --- | --- |
| Rev no. | Revision remark |
|  | Transformer Data |
| AA | Type of transformer (single or three-phase, power, furnace, etc) |
|  |  | Power transformer |  | 3-phase |  | 1-phase |
|  |  | Arc furnace |  | 3-phase |  | 1-phase |
|  |  | Other |  | 3-phase |  | 1-phase |
| AB | Rated power MVA | Capacity below neutral: | Reduced Full |
| AC | Rated voltage ratio, frequency, regulating range and connection |
|  | Voltage (HV/LV): |  | / |  | kV | Frequency: 60 Hz / 50 Hz |
|  | Regulating range: | ± % / | x |  | % of HV / LV winding |
|  | Connection (HV/LV): (Y, (, Auto) |  | / |  |  |
| AD | The OLTC is placed | in the line end of | in the middle of | in the neutral point of |
|  |  | the HV winding | the LV winding |  |
| AE | Insulation level of the OLTC | Note: Values given in the Technical Guide for the chosen OLTC must not be exceeded |
|  | 1.2/50 (s impulse withstand voltage — power frequency withstand voltage |
|  | Phase to earth |  | - |  | Between phases (b1) |  | - |  |
|  | Neutral point to earth |  | - |  | Across regulating winding (a2) |  | - |  |
| AG | Type of switching |  |  |
|  | Linear | Plus/minus | Coarse/fine |
| AH | Leakage induction through coarse and fine winding |  |
|  | Specify the leakage inductance through the coarse and fine windings in series (L) mH. |  |
|  | On-load Tap-Changer Data |
| BA | OLTC type designation |
|  | UZ |  | / 600 A (Compare Technical Guide) |
| BC | Number of electrical positions | 33 | Other |
| BD | Rated phase step voltage | V |
| BE | Rated through current (=max phase current in the OLTC winding) A |
| BF | Overload requirements |
|  |  | According to IEC 60354 |
|  |  | According to IEEE C57.91-1995 |
|  |  | Other requirements |
| BG | Data for tap-changer tank |
|  | Flange connected to the transformer | by welding |  | by bolting |
|  | Reinforced barrier | Yes |  |  |
|  | Flange only for separate oil conservator (UZE/UZF) |
| BH (CF) | Effective number of turns |
|  | Effective number of turns connected in regulating winding with OLTC in lowest position on the indication plate (furthest counter clockwise position) |
|  | Linear Max | Linear Min | Plus / Minus Max | Plus / Minus Min | Coarse / Fine Max | Coarse / Fine Min |
| BJ | Short circuit current |
|  | Rms value |
|  | Max. 8 kA, 3 s; 20 kA, peak value |
|  | Max. 12 kA, 2 s; 30 kA peak value (requires special magnetic yoke) |
| BK | Languages for plates |
|  | English | Spanish | French | Other |
| BL | Tie-in resistor | No | Yes | Calculated by ABB. |
|  | Needed only if recovery voltage of the change-over selector exceeds 40 kV. |  | Give winding layout, winding connections and capacitances between windings. The tie-in resistors are placed in the transformer tank. |
| BM | Oil level indicator |
|  | Yes, with Hi/Lo contacts (QUALITROL cat.#035-068-01) | NOTE: UZE always make selection. UZF make selection only if conservator ordered (see section BY) |
|  | Yes, with Lo/MaxLo contacts |  |
|  | Flange only provided |  |
| BN | Surface treatment |
|  |  | Rust protection primer outside & inside, White finishing coat inside. |
|  |  | Other painting |
| BO | Cable lugs |
|  | Catalogue No. | Hole diameter (mm) | For cable area (mm2) |  |  |
|  | LL 114 003-A | 11 | 50 |  |  |
|  | LL 114 003-B | 13 | 70 |  |  |
|  | LL 114 003-C | 15 | 95 |  |  |
|  | LL 114 003-D | 17 | 120 |  |  |
|  | LL 114 003-E | 19 | 150 |  |  |
|  | LL 114 003-F | 21 | 185 |  |  |
|  | Additional lugs: 0 pcs |  |  |
| BS | Drain valve |
|  |  | 1.0” NPT inside thread globe with sampling valve |
|  |  | 1.0” NPT inside thread globe without sampling valve |
|  |  | 1.5” NPT inside thread globe with sampling valve |
|  |  | 1.5” NPT inside thread globe without sampling valve |
|  |  | Other |
|  | Extra vent for oil filling | No. | Yes |
| BT | Supervisory devices |
|  | For pressure relay | Vertical distance H between the pressure relay |
|  |  | and the oil level in the conservator m |
|  |  | Note: If a one-way breather is used, add 4 m. |
|  | Temperature lock out switch |  | No |
|  |  |  | Only housing |
|  |  |  | Temperature switch –25 °C |
|  |  |  | Temperature switch –40 °C |
| BU | Provision for Qualitrol liquid temp. gauge 0.5” NPT inside thread thermal well |  | No |
|  |  |  | Yes |
| BV | Pressure Relief Device (PRD) |  | PRD with alarm and flag |
|  |  |  | Flange only |
| BX | Upper oil valve (1” NPT) [Also used as upper oil filtration valve outlet] |  | No, provision only |
|  |  |  | Yes, supply valve |
| BY | Oil-conservator – type UZF only |  | Provisions only (flange for oil conservator) |
|  |  |  | Oil conservator on the OLTC roof |
|  | Standard Positioning of Accessories If other positions for accessories are required, please indicate on sketch. |
|  | Motor Drive Data |
| CA | Door hinged on | Left side | Right side |
| CC | Voltage for motor |
|  |  | 1~60 Hz 120 V |  | 1~60 Hz 240 V |
|  |  | Other |
| CD | Voltage for control circuits |
|  |  | 1~60 Hz 120 V |  | Other |
| CE | Voltage for heater |
|  |  | 120 V |  | Other |
| CF | Marking of mechanical position indicator (front plate) |
|  |  | Lowest position marked 1 |  | Middle position marked N |  | Middle position marked N |  | Other (fill in) |
|  |  |  |  |  |  |  |  | N |  |  |  |  | N |  |  |  |  |  |
|  |  |  |  |  |  |  | - |  | + |  |  | L |  | R |  |  |  |  |
|  | 1 |  | n | n |  | n | n |  | n |  |  |  |
|  | A "RAISE" command of the motor-drive means a clockwise rotation of dial. |
| CG | Type of terminal blocks |
|  |  | Manufacturer | Type | Max. no of terminals |  |
|  |  | General Electric | EB-25 | 72 |  |
|  |  | Other |
|  | Note: More than the above number of terminals means special design and additional price. |
| CH | Step by step operation |  | No |  | Yes |
| CK | Extra heater |  | No |  | Yes, with thermostat and switch |
| CL | Convenience outlet |  | Yes, with GFI |  | No |
| CN | Multi-position switches |
|  | Total number of required multi-position switches must be noted. |
|  | Numbers required | Type | Symbol | Occupies space for contact rows | Numbers required | Type | Symbol | Occupies space for contact rows |
|  |  | Potentiometer position transmitter |  | 1 |  | Step switch* for parallel control |  | 2 |
|  |  | Break before make |  | 1 |  | Follower switch for parallel control |  | 2 |
|  |  | Make before break |  | 1 |  | Contact row for section CT |  | 1 |
|  |  |  |  |  |  | * Odd/even switch |  |
|  | Master switch for parallel control is a break before make multi-position switch. Max. number of contact rows: 12, without through positions (UZ.L) 11, with through positions (UZ.R, UZ.D) 10, with through positions and one contact row occupied for running-through protection Incon transmitter (if specified) occupies spaces for 4 contact rows. |
|  | The following UZ types occupy one contact row for running-through protection: |
|  | Types | Number of positions |  |
|  | UZ.R | 9, 11, 13, 15, 17, 25, 27 |  |
| CO | Resistance in ohms per step for position transmitter |
|  |  | None required |  | 10 Ω, 5 W |  | Other |
| CP | Measuring amplifier for remote position indicator |
|  | (Standard 10 Ω /step, See clause CO) |
|  |  | No | 0-1 mA |
|  |  | Yes, one (for 13 to 35 positions only) | 0-5 mA |
|  |  | Yes, numbers required | 0-10 mA |
|  |  | 0-20 mA |
|  |  | 4-20 mA |
|  |  | Auxiliary voltage: |
|  |  | DC 24-130 V |
|  |  | AC 110-120 V |
|  |  | AC 220-240 V |
| CR | Remote Position Transmitter |
|  |  | None Required |
|  |  | Provision only for Incon 1292-K |
|  |  | Provision only other (Mfg and Model) |
|  |  | Provide Transmitter Incon 1292-K |
|  |  | Provide Transmitter other (Mfg and Model) |
| CS | Electrically resettable drag hand (120 V 60 Hz supply required) |
|  |  | No |  | Yes |  |  |
| CT | Coder |
|  |  | No |
|  |  | Yes, BCD coded 1, 2, 4, 8, 10, 20 |
|  |  | Yes, Binary Coder (BC) 1, 2, 4, 8, 16, 32 |
|  | Note: 1 “contact row for coder” at section CN is also needed; occupies totally 1 contact row. |
|  |  | If further requirements please state below: |

# Text boxes

BT

Beta Relay

BS

Drain Valve

BS

Extra vent for oil filling

BU

Provision for temperature gauge

BM

Oil Level Indicator UZE

BV

Pressure Relief Device

Breather UZ (standard)

BX

1” NPT Nipple UZE/UZF