## Telegram 1
68 | Start char
E8 | Length
E8 | Length
68 | Start char
08 | RSP_UD
00 | Primary address
72 | Variable data respond
34 12 00 00 | Serial number | 00001234
42 04 | Manufacturer | ABB
20 | Version
02 | Medium | Electricity
1C | Access number
00 | Status
00 00 | Signature
0E | DIF | Data is 12 digit BCD
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
55 53 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
10 | DIFE | Tariff = 1
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
77 10 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
20 | DIFE | Tariff = 2
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
93 04 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
30 | DIFE | Tariff = 3
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
70 21 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Tariff = 0
10 | DIFE | Tariff = 4
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
14 16 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
40 | DIFE | Unit=1 => Export
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
02 08 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
50 | DIFE | Tariff = 1, Unit = 1 => Export
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
41 01 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
60 | DIFE | Tariff = 2, Unit = 1 => Export
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
72 02 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
70 | DIFE | Tariff = 3, Unit = 1 => Export
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
39 01 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Tariff = 0, Unit = 1 => Export
10 | DIFE | Tariff = 4
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
48 02 00 00 00 00 | Data
01 | DIF | Data is 8 bit integer
FF | VIF | Next byte is manufacturer specific
93 | VIFE | Active tariff
00 | VIFE | Status: No error
04 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A0 | VIFE | CT numerator
00 | VIFE | Status: No error
C8 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A1 | VIFE | VT numerator
15 | VIFE | Status: No data available
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A2 | VIFE | CT denominator
00 | VIFE | Status: No error
05 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A3 | VIFE | VT denominator
15 | VIFE | Status: No data available
00 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A6 | VIFE | Error flags
00 | VIFE | Status: No error
00 00 00 00 00 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A7 | VIFE | Warning flags
00 | VIFE | Status: No error
00 00 00 00 00 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A8 | VIFE | Information flags
00 | VIFE | Status: No error
00 00 00 00 00 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A9 | VIFE | Alarm flags
00 | VIFE | Status: No error
00 00 00 00 00 00 00 00 | Data
0D | DIF | Variable length of data
FD | VIF | Extension of VIF-codes
8E | VIFE | Firmware version
00 | VIFE | Status: No error
09 37 2E 30 2E 37 31 2E 31 42 | Data
0D | DIF | Variable length of data
FF | VIF | Next byte is manufacturer specific
AA | VIFE | Type designation
00 | VIFE | Status: No error
0B 30 30 31 2D 33 35 33 20 34 32 42 | Data
1F | DIF | More data in next telegram
A1 | Checksum
16 | End

## Telegram 2
68 | Start char
F2 | Length
F2 | Length
68 | Start char
08 | RSP_UD
00 | Primary address
72 | Variable data respond
34 12 00 00 | Serial number
42 04 | Manufacturer | ABB
20 | Version
02 | Medium | Electricity
1D | Access number
00 | Status
00 00 | Signature
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
98 | VIFE | Power fail counter
00 | VIFE | Status: No error
12 00 00 00 | Data
04 | DIF | Data is 32 bit integer
A9 | VIF | Power with 2 decimals
00 | VIFE | Status: No error
9D 3B 04 00 | Data
04 | DIF | Data is 32 bit integer
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
CB 66 01 00 | Data
04 | DIF | Data is 32 bit integer
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
14 6B 01 00 | Data
04 | DIF | Data is 32 bit integer
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
BF 69 01 00 | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
A9 | VIF | Power with 2 decimals
00 | VIFE | Status: No error
98 FA FF FF | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
1D 00 00 00 | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
F2 FB FF FF | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
8B FE FF FF | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
A9 | VIF | Power with 2 decimals
00 | VIFE | Status: No error
9D 3B 04 00 | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
CB 66 01 00 | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
14 6B 01 00 | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
BF 69 01 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
FD 08 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
FC 08 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
04 09 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
85 | VIFE | L1 - L2
00 | VIFE | Status: No error
8D 0F 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
86 | VIFE | L3 - L2
00 | VIFE | Status: No error
93 0F 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
87 | VIFE | L1 - L3
00 | VIFE | Status: No error
9D 0F 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
D9 | VIFE | Ampere with 3 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
96 0F 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
D9 | VIFE | Ampere with 3 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
C7 0F 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
D9 | VIFE | Ampere with 3 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
AB 0F 00 00 | Data
0A | DIF | Data is 4 digit BCD
FF | VIF | Next byte is manufacturer specific
D9 | VIFE | Frequency with 2 decimals
00 | VIFE | Status: No error
80 49 | Data
1F | DIF | More data in next telegram
FC | Checksum
16 | End

## Telegram 3
68 | Start char
C1 | Length
C1 | Length
68 | Start char
08 | RSP_UD
00 | Primary address
72 | Variable data respond
34 12 00 00 | Serial number
42 04 | Manufacturer | ABB
20 | Version
02 | Medium | Electricity
1E | Access number
00 | Status
00 00 | Signature
02 | DIF | Data is 16 bit integer
FF | VIF | Next byte is manufacturer specific
E0 | VIFE | Power factor with 3 decimals
00 | VIFE | Status: No error
E8 03 | Data
02 | DIF | Data is 16 bit integer
FF | VIF | Next byte is manufacturer specific
E0 | VIFE | Power factor with 3 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
E8 03 | Data
02 | DIF | Data is 16 bit integer
FF | VIF | Next byte is manufacturer specific
E0 | VIFE | Power factor with 3 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
E8 03 | Data
02 | DIF | Data is 16 bit integer
FF | VIF | Next byte is manufacturer specific
E0 | VIFE | Power factor with 3 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
E8 03 | Data
02 | DIF | Data is 16 bit integer
FF | VIF | Next byte is manufacturer specific
D2 | VIFE | Phase angle power with 1 decimal
00 | VIFE | Status: No error
00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
45 07 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
90 | DIFE | Tariff = 1
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
39 01 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
A0 | DIFE | Tariff = 2
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
52 02 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
B0 | DIFE | Tariff = 3
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
49 01 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE
50 | DIFE | Tariff = 4, Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
04 02 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
92 08 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
D0 | DIFE | Tariff = 1, Unit=1 => Export
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
38 02 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
E0 | DIFE | Tariff = 2, Unit=1 => Export
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
23 02 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
F0 | DIFE | Tariff = 3, Unit=1 => Export
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
65 01 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
50 | DIFE | Tariff = 4, Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
65 02 00 00 00 00 | Data
01 | DIF | Data is 8 bit integer
FF | VIF | Next byte is manufacturer specific
AD | VIFE | Number of elements
00 | VIFE | Status: No error
03 | Data
01 | DIF | Data is 8 bit integer
FF | VIF | Next byte is manufacturer specific
97 | VIFE | Current quadrant
00 | VIFE | Status: No error
04 | Data
01 | DIF | Data is 8 bit integer
FF | VIF | Next byte is manufacturer specific
97 | VIFE | Current quadrant
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
01 | Data
01 | DIF | Data is 8 bit integer
FF | VIF | Next byte is manufacturer specific
97 | VIFE | Current quadrant
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
04 | Data
01 | DIF | Data is 8 bit integer
FF | VIF | Next byte is manufacturer specific
97 | VIFE | Current quadrant
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
04 | Data
1F | DIF | More data in next telegram
CB | Checksum
16 | End

## Telegram 4
68 | Start char
E8 | Length
E8 | Length
68 | Start char
08 | RSP_UD
00 | Primary address
72 | Variable data respond
34 12 00 00 | Serial number
42 04 | Manufacturer | ABB
20 | Version
02 | Medium | Electricity
1F | Access number
00 | Status
00 00 | Signature
81 | DIF | Data is 8 bit integer
40 | DIFE | Unit=1 => Output 1
FD | VIF | Extension of VIF-codes
9A | VIFE | Digital output
00 | VIFE | Status: No error
00 | Data
81 | DIF | Data is 8 bit integer
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Output 2
FD | VIF | Extension of VIF-codes
9A | VIFE | Digital output
00 | VIFE | Status: No error
00 | Data
81 | DIF | Data is 8 bit integer
C0 | DIFE | Unit=1
40 | DIFE | Unit=3 => Input 3
FD | VIF | Extension of VIF-codes
9B | VIFE | Digital input
00 | VIFE | Status: No error
00 | Data
81 | DIF | Data is 8 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Input 4
FD | VIF | Extension of VIF-codes
9B | VIFE | Digital input
00 | VIFE | Status: No error
00 | Data
C1 | DIF | Storage no = 1, Data is 8 bit integer
C0 | DIFE | Unit=1
40 | DIFE | Unit=3 => Input 3
FD | VIF | Extension of VIF-codes
9B | VIFE | Digital input
00 | VIFE | Status: No error
00 | Data
C1 | DIF | Storage no = 1, Data is 8 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Input 4
FD | VIF | Extension of VIF-codes
9B | VIFE | Digital input
00 | VIFE | Status: No error
00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1
40 | DIFE | Unit=3 => Counter 3
FD | VIF | Extension of VIF-codes
E1 | VIFE | Cumulating counter
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Counter 4
FD | VIF | Extension of VIF-codes
E1 | VIFE | Cumulating counter
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
0E | DIF | Data is 12 digit BCD
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
F2 | VIFE | Resettable register
00 | VIFE | Status: No error
55 53 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
40 |  | Unit=1 => Export
84 |  | Energy with 2 decimals
FF |  | Next byte is manufacturer specific
F2 |  | Resettable register
00 | VIFE | Status: No error
02 08 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 |  | Unit=0
40 |  | Unit=2 => Reactive
84 |  | Energy with 2 decimals
FF |  | Next byte is manufacturer specific
F2 |  | Resettable register
00 | VIFE | Status: No error
45 07 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 |  | Unit=1 => Export
40 |  | Unit=2 => Reactive
84 |  | Energy with 2 decimals
FF |  | Next byte is manufacturer specific
F2 |  | Resettable register
00 | VIFE | Status: No error
92 08 00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF |  | Next byte is manufacturer specific
F1 |  | Reset counter for energy
00 | VIFE | Status: No error
00 00 00 00 | Data
84 | DIF | Data is 32 bit integer
40 |  | Unit=1 => Export
FF |  | Next byte is manufacturer specific
F1 |  | Reset counter for energy
00 | VIFE | Status: No error
00 00 00 00 | Data
84 | DIF | Data is 32 bit integer
80 |  | Unit=0
40 |  | Unit=2 => Reactive
FF |  | Next byte is manufacturer specific
F1 |  | Reset counter for energy
00 | VIFE | Status: No error
00 00 00 00 | Data
84 | DIF | Data is 32 bit integer
C0 |  | Unit=1 => Export
40 |  | Unit=2 => Reactive
FF |  | Next byte is manufacturer specific
F1 |  | Reset counter for energy
00 | VIFE | Status: No error
00 00 00 00 | Data
0E | DIF | Data is 12 digit BCD
FF | VIF | Next byte is manufacturer specific
F9 | VIFE | Extension of manufacturer specific VIFE-codes
C4 | VIFE | Energy in CO2, kg with 3 decimals
00 | VIFE | Status: No error
60 35 05 00 00 00 | Data
0E | DIF | Data is 12 digit BCD
FF | VIF | Next byte is manufacturer specific
F9 | VIFE | Extension of manufacturer specific VIFE-codes
C9 | VIFE | Energy in currency with 2 decimals
00 | VIFE | Status: No error
56 53 00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A4 | VIFE | CO2 conversion factor (kg * 10-3 /kWh)
00 | VIFE | Status: No error
E8 03 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A5 | VIFE | Currency conversion factor (curr * 10-3 /kWh)
00 | VIFE | Status: No error
E8 03 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
94 62 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
02 08 00 00 00 00 | Data
1F | DIF | More data in next telegram
6B | Checksum
16 | End

## Telegram 5
68 | Start char
F7 | Length
F7 | Length
68 | Start char
08 | RSP_UD
00 | Primary address
72 | Variable data respond
34 12 00 00 | Serial number
42 04 | Manufacturer | ABB
20 | Version
02 | Medium | Electricity
20 | Access number
00 | Status
00 00 | Signature
0E | DIF | Data is 12 digit BCD
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
42 21 00 00 00 00 | Data
0E | DIF | Data is 12 digit BCD
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
18 17 00 00 00 00 | Data
0E | DIF | Data is 12 digit BCD
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
97 14 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
40 | DIFE | Unit=1 => Export
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
47 04 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
40 | DIFE | Unit=1 => Export
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
67 02 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
40 | DIFE | Unit=1 => Export
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
88 00 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
51 02 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
49 02 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
44 02 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
92 02 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
99 02 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
00 03 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
56 24 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
31 20 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
08 18 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
47 04 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
67 02 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
88 00 00 00 00 00 | Data
1F | DIF | No more data in next telegram
33 | Checksum
16 | End

## Telegram 6
68 | Start char
CE | Length
CE | Length
68 | Start char
08 | RSP_UD
00 | Primary address
72 | Variable data respond
34 12 00 00 | Serial number
42 04 | Manufacturer | ABB
20 | Version
02 | Medium | Electricity
21 | Access number
00 | Status
00 00 | Signature
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 6 = Net
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
C9 11 00 00 00 00 00 00 | Data
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 6 = Net
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
9E 06 00 00 00 00 00 00 | Data
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 6 = Net
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
AA 05 00 00 00 00 00 00 | Data
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 6 = Net
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
81 05 00 00 00 00 00 00 | Data
87 | DIF | Data is 64 bit integer
C0 | DIFE | Unit=1 =>
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 7 = Net reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
6D FF FF FF FF FF FF FF | Data
87 | DIF | Data is 64 bit integer
C0 | DIFE | Unit=1 =>
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 7 = Net reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
D8 FF FF FF FF FF FF FF | Data
87 | DIF | Data is 64 bit integer
C0 | DIFE | Unit=1 =>
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 7 = Net reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
CE FF FF FF FF FF FF FF | Data
87 | DIF | Data is 64 bit integer
C0 | DIFE | Unit=1 =>
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 7 = Net reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
C9 FF FF FF FF FF FF FF | Data
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=8 => Net apparent
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
74 15 00 00 00 00 00 00 | Data
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=8 => Net apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
D8 07 00 00 00 00 00 00 | Data
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=8 => Net apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
E3 06 00 00 00 00 00 00 | Data
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=8 => Net apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
B8 06 00 00 00 00 00 00 | Data
0F | DIF | No more data in next telegram
E7 | Checksum
16 | End