## Type Test Report
[5 empty] | Date of issue: | 2011-12-28
Type Test Report
[5 empty] | Serial No.: | 3GH093811T2206
Customer:
[5 empty] | Type: | M3BP 112MB 6
[5 empty] | Product Code: | 3GBP113322-_DB
Customer ref.:
Rating:
|  | V |  | Hz | kW | r/min | A | cos j | Duty
3~Motor |  | 690 | Y | 50 | 2.2 | 950 | 3.1 | 0.69 | S1
Insul.cl.F |  | 400 | D | 50 | 2.2 | 950 | 5.5 | 0.69 | S1
IP55 |  | 460 | D | 60 | 2.2 | 1160 | 4.7 | 0.68 | S1
|  | 50Hz : | IE2 - 82,5(100%) - 83,8(75%) - 81,7(50%)
Resistance |  |  |  |  | Insulation resistance at |  | 27.2 | ºC | Overload
Line |  | Ambient: | 23.5 | ºC | R > 2000 Mohm | 1000 | V |  | Current | 150% | 120s
U1 - V1 |  | 4.425 | W | [5 empty] | Torque | 160% | 15s
U1 - W1 |  | 4.424 | W | [5 empty] | Speed | 120% | 120s
V1 - W1 |  | 4.424 | W
[5 empty] | High-voltage test winding |  | 2400 | V | 60 | s
Test | Torque | Line |  |  | Input |  | Output
| [Nm] | U[V] |  | f[Hz] | I[A] | P1 [kW] | P2 [kW] | n[r/min] | cos j | h [%]
No load test |  | 400 | D | 50 | 3.4 | 0.2 |  | 1000 | 0.08
Locked rotor test |  | 108.5 | D | 50 | 5.5 | 0.49 |  | 0 | 0.47
Thermal test ( 100% load ) | 22.1 | 400 | D | 50 | 5.4 | 2.69 | 2.2 | 951 | 0.71 | 81.7
Partial load points:
~75% load | 16.3 | 400 | D | 50 | 4.2 | 1.99 | 1.65 | 965 | 0.67 | 83
~50% load | 10.8 | 400 | D | 50 | 3.7 | 1.36 | 1.1 | 977 | 0.52 | 80.8
~25% load | 5.3 | 400 | D | 50 | 3.3 | 0.76 | 0.55 | 989 | 0.33 | 72.4
Temperature rise at rated load. |  |  |  | [oC] | [K] | Method |  | Measurement method
|  | Stator winding : |  |  | 48.3 | 3 |  | 1 Resistance
|  | Frame : |  |  | 28.2 | 3 |  | 2 Thermometer
|  | Bearing D-end : |  |  | 29.8 | 3 |  | 3 Thermocouples
|  | Ambient Temperature : |  | 25 |  | 3
Manufactured and tested in accordance with rules of IEC 60034-1 and IEC 60034-2-1.
PLL determined from residual loss.
On behalf of customer
On behalf of manufacturer |  | Date of test |  |  | 2009-10-06
[7 empty] | Telephone | +34 93 728 85 00
Tested by Asea Brown Boveri, S.A., Fabrica Motores , 08192 Sant Quirze del Valles , Spain | [6 empty] | Telefax | +34 93 728 85 33
Computer print-out valid without signature.
ABB, Motors and Generators
www abb.com/motors&generators

## Test Report
[5 empty] | Date of issue: | 2011-09-21
Test Report
[5 empty] | Serial No.: | 3GV1010461793001
Customer: |  |  |  |  | Tag No.: | PM52897-A |  |  | Manufactured and
[5 empty] | Order No.: | 10461793-B |  |  | tested according to
[5 empty] | Type: | M3AA 280SMA 4 IMV3/IM3031 |  |  | DET NORSKE
[5 empty] | Product Code: | 3GAA282031-ADG |  |  | VERITAS.
[5 empty] | Protection type: | Ex nA II T3
[5 empty] | Cert. No.: | LCIE XXXX
Customer ref.: |  |  |  |  | Marine Cert. No.: | VSA11-XXXX
Rating:
|  | V |  | Hz | kW | r/min | A | cos j | Duty
3~Motor |  | 400 | D | 50 | 75 | 1478 | 135 | 0.85 | S1
Insul.cl.F |  | 690 | Y | 50 | 75 | 1478 | 78.2 | 0.85 | S1
IP55 |  | 415 | D | 50 | 75 | 1480 | 133 | 0.83 | S1
Ambient temp. -20 - +45ºC |  | 460 | D | 60 | 75 | 1782 | 116 | 0.85 | S1
Eff class IE2 |  | 50Hz : | IE2 - 94,3(100%) - 94,9(75%) - 94,6(50%)
|  | 60Hz : | IE2 - 94,8(100%) - 94,9(75%) - 94,1(50%)
Resistance |  |  |  |  | Insulation resistance at |  | 22.5 | ºC | Overload
Line |  | Ambient: | 22.7 | ºC | R > 2000 Mohm | 1000 | V |  | Current | 150% | 120s
U1 - V1 |  | 0.04281 | W |  | Heaters : | O.K. |  |  | Torque | 160% | 15s
U1 - W1 |  | 0.04243 | W |  | Thermistors : | O.K. |  |  | Speed | 120% | 120s
V1 - W1 |  | 0.04245 | W |  | PT100 : | O.K.
[5 empty] | High-voltage test winding |  | 2400 | V | 60 | s
| Heaters : | 2117 | W |  |  | Heaters : | O.K.
| Thermistors : | 186 | W |  |  | Thermistors : | O.K.
| PT100 : | 108.9 | W |  |  | PT100 : | O.K.
Test | Torque | Line |  |  | Input |  | Output
| [Nm] | U[V] |  | f[Hz] | I[A] | P1 [kW] | P2 [kW] | n[r/min] | cos j | h [%]
No load test |  | 400.6 | D | 50 | 48 | 1.45 |  | 1500 | 0.04
Locked rotor test |  | 71.1 | D | 50 | 119.7 | 5.61 |  | 0 | 0.38
Thermal test ( 100% load ) | 484.9 | 400 | D | 50 | 135.5 | 79.59 | 75 | 1477 | 0.84775 | 94.24
Partial load points:
~75% load | 362.5387 | 400 | D | 50 | 105.8 | 59.51 | 56.34 | 1484 | 0.81189 | 94.67
~50% load | 242.3855 | 400 | D | 50 | 79.9 | 40.04 | 37.82 | 1490 | 0.72328 | 94.46
~25% load | 122.1927 | 400 | D | 50 | 58.6 | 20.79 | 19.13 | 1495 | 0.51189 | 92.05
Temperature rise at rated load. |  |  |  | [oC] | [K] | Method |  | Measurement method
|  | Stator winding : |  |  | 73.5 | 1 |  | 1 Resistance
|  | Frame : |  |  | 52 | 2 |  | 2 Thermometer
|  | Bearing D-end : |  |  | 66 | 2 |  | 3 Thermocouples
|  | Rotor : |  |  | 70.3 | 2
|  | Ambient Temperature : |  | 25 |  | 2
|  | ↓ |  | → |  |  |  |  | Sound pressure 100% load, LpA [dB]:
Vibration: | D-end | [7 empty] | Starting current (IS / IN) :
| N-end | [7 empty] | Locked rotor torque (Tl / TN) :
| Axial | [7 empty] | Breakdown torque (Tb / TN) :
Pull-up torque (Tu / TN) :
Manufactured and tested in accordance with rules of IEC 60034-1 and IEC 60034-2-1.
PLL determined from residual loss.
On behalf of customer
On behalf of manufacturer |  | Date of test |  |  | 2010-05-17
[7 empty] | Telephone | +46 (0)21 32 90 00
Tested by ABB AB, LV Motors, 721 70 Västerås, Sweden | [6 empty] | Telefax | +46 (0)21 32 90 22
Computer print-out valid without signature.
ABB, Motors and Generators
www abb.com/motors&generators