## Slide 1: New Busbar PSHs

## Slide 2: New Busbar PSHs
In order to improve the PSH busbars deliveries and satisfy better the demand, value chain will be changed having identified a new supplier. Availalbility by Q2 2024.
Impacts:
New SKUs 12 digit, keeping same Product Description (PSH)- see below ref table
Difference respect previous product in appearance with comparable performances.
Scope
Same busbar Portfolio
 | OLD SKU | NEW SKU | DESCRIPTION
BUSBARS | 2CDL110001R1012 | 2CDL111001R1012 | PSH1/12
 | 2CDL110001R1060 | 2CDL111001R1060 | PSH1/60
 | 2CDL120001R1012 | 2CDL121001R1012 | PSH2/12, Endcaps included
 | 2CDL120001R1058 | 2CDL121001R1058 | PSH2/58
 | 2CDL130001R1012 | 2CDL131001R1012 | PSH3/12, Endcaps included
 | 2CDL130001R1060 | 2CDL131001R1060 | PSH3/60
 | 2CDL140001R1012 | 2CDL141001R1012 | PSH4/12, Endcaps included
 | 2CDL140001R1058 | 2CDL141001R1058 | PSH 4/58N
 | 2CDL140001R1060 | 2CDL141001R1060 | PSH4/60
ACCESSORIES | 2CDL100001R0001 | 2CDL101001R0001 | PSH-END
 | 2CDL100011R0011 | 2CDL101011R0011 | PSH-END 1.1
 | 2CDL100001R0002 | 2CDL101001R0002 | PSH-END 1

## Slide 3: New Busbar PSHs
Deviations: General & Technical Data sheet
 |  |  | Busbars PSH (NEW) | Busbars PSH (OLD)
Suitable for |  |  | MCB: SH200 RCD: FH200 RCBO: DSH201 LBS: SHD200 | MCB: SH200 RCD: FH200 RCBO: DSH201 LBS: SHD200
Electrical Data | Standards |  | IEC/EN 61439-1 | IE/EN 60947-1
 | Approvals |  | - | 
 | Rated Voltage | V | 440 | 400V
 | Rated Frequency | Hz | 50 | 50/60, DC
 | Current carrying capacity / phase (35ºC ambient temperature) | A | 63 | 63
 | Short Circuit whitstand capacity |  | Icc = 10 kA protected by SH200 MCB's | 25 kA protected by fuse NH3 350 A gG 500V
Mechanical Data | Housing |  | light grey, RAL 7035 | light grey, RAL 7035
 | Environment conditions |  | IEC/EN 60068 | IEC/EN 60068
 | Overvoltage category |  | III | III
 | Pollution degree |  | 2 | 2
Installation | Cross-Section Busbar |  | 10 mm2 | 10 mm2
 | Mounting position |  | Top / bottom | optional
 | Supply |  | Feed on terminal of the device: 16 mm2 flexible in MCB terminal 25 mm2 rigid in MCB terminal | Feed on terminal of the device
Accessories | Shock protection caps |  | Under check | BSK, SZ-BSK
 | Feed-in terminals |  | Under Check | AST, SZ-ESK
 | End cap |  | PSH-END PSH-END 1 PSH-END 1.1 | PSH-END PSH-END 1 PSH-END 1.1
New Busbars are Made in China, previous Made in (North) Macedonia
Lead time of new Busbar is 4/6 weeks vs previous one >8 weeks
New Busbars have been tested according latest internal procedures, and performances are comparable with Old ones (temperature rise, creepage,..)
New Busbars have different L&F, reason why new SKU is associated
New Busbars will have their own End caps, even if Product description is kept as the same

## Slide 4: New Busbar PSHs
NEW ONE
NEW ONE
NEW ONE
NEW ONE
NEW ONE
NEW ONE
A bit wider
Less high and wide
PSH 3 PHASES
PSH 1 PHASE
Overview
NEW ONE
CURRENT ONE
CURRENT ONE
CURRENT ONE
CURRENT ONE
CURRENT ONE
CURRENT ONE
CURRENT ONE

## Slide 5: New Busbar PSHs
Actual Model
New Model
What’s changing? : PSH1 (single phase)
Insulation is bit bigger than previous (16,8mm vs 14,7mm) but this will not cause issues if mounted as in the pictures (correct way)

## Slide 6: New Busbar PSHs
Actual Model
New Model
What’s changing? : PSH2 (double phase)
Comparable to the old ones, same access for the cable when busbar is installed

## Slide 7: New Busbar PSHs
Actual Model
New Model
What’s changing? : PSH3 (triple phase)
Comparable to the old ones, same access for the cable when busbar is installed

## Slide 8: New Busbar PSHs
Actual Model
New Model
What’s changing? : PSH4 (double phase)
Comparable to the old ones, same access for the cable when busbar is installed

## Slide 9: New Busbar PSHs
What’s changing?: End Caps for PSH2 and PSH3
NEW ONE
ACTUAL ONE
PSH- END
PSH- END

## Slide 10: New Busbar PSHs
What’s changing?: End Caps for PSH4
NEW ONE
ACTUAL ONE
PSH- END 1
PSH- END 1

## Slide 11: New Busbar PSHs
What’s changing?: End Caps for PSH1
NEW ONE
ACTUAL ONE
PSH- END 1.1
PSH- END 1.1