## Test Report
[5 empty] | Date of issue: | 2015-06-01
Test Report
Serial No.:
Customer:
[5 empty] | Type: | M3GP 180MLA 4
[5 empty] | Product Code: | 3GGP182410-ADL
[5 empty] | Protection type: | Ex tb IIIB/C T125C Db
[5 empty] | Cert. No.: | LCIE 13 ATEX 3067 X
IECEx LCIE 13.0047 X
Customer ref.:
Rating:
|  | V |  | Hz | kW | r/min | A | cos j | Duty
3~Motor |  | 690 | Y | 50 | 18.5 | 1481 | 20.1 | 0.83 | S1
Insul.cl.F |  | 400 | D | 50 | 18.5 | 1481 | 34.9 | 0.83 | S1
IP65 |  | 415 | D | 50 | 18.5 | 1482 | 33.8 | 0.82 | S1
Eff class IE3 |  | 440 | D | 60 | 18.5 | 1781 | 31.2 | 0.83 | S1
|  | 460 | D | 60 | 18.5 | 1783 | 30.3 | 0.82 | S1
50Hz: IE3-92,6%(100%)-93,3%(75%)-92,9%(50%)
60Hz: IE3-93,6%(100%)
Resistance |  |  |  |  | Insulation resistance at |  | 84.7 | ºC | Overload
Line |  | Ambient: | 23.5 | ºC | 2000 MΩ | 1000 | V |  | Torque 160% 15s
U1 - V1 |  | 0.255 | W | [5 empty] | Speed 120% 120s
U1 - W1 |  | 0.2557 | W | [5 empty] | Current 150% 15s
V1 - W1 |  | 0.255 | W
[5 empty] | High-voltage test winding |  | 1900 | V | 60 | s
Test | Torque | Line |  |  | Input |  | Output
| [Nm] | U[V] |  | f[Hz] | I[A] | P1 [kW] | P2 [kW] | n[r/min] | cos j | h [%]
No load test |  | 400.6 | D | 50 | 13.248 | 0.445 |  | 1498 | 0.048
Locked rotor test |  | 84.4 | D | 50 | 34.91 | 1.729 |  | 0 | 0.338
Thermal test (100% load) | 119.7 | 400.7 | D | 50 | 34.88 | 19.96 | 18.5 | 1480.6 | 0.826 | 92.7
Partial load points:
~75% load | 89.2 | 400.1 | D | 50 | 27.34 | 14.88 | 13.87 | 1486.1 | 0.785 | 93.3
~50% load | 59.8 | 399.9 | D | 50 | 20.74 | 9.94 | 9.25 | 1490.3 | 0.692 | 93
~25% load | 29.7 | 400.6 | D | 50 | 15.58 | 5.14 | 4.62 | 1495.3 | 0.476 | 90.1
Temperature rise at rated load. |  |  |  | [oC] | [K] | Method |  | Measurement method
|  | Stator winding : |  |  | 56.8 | 1 |  | 1 Resistance
|  | Frame : |  |  | 25.6 | 2 |  | 2 Thermocouples
|  | Bearing D-end : |  |  | 31.2 | 2 |  | 3 Thermometer
|  | Rotor: |  |  | 70 | 3
|  | Ambient Temperature : |  | 25 |  | 2
These tests have been carried out on motor no. 3G1P141700178, on date 2014-06-19
which is identical in design with the above.
Manufactured and tested in accordance with rules of IEC 60034-1 and IEC 60034-2-1.
PLL determined from residual loss.
On behalf of customer
On behalf of manufacturer |  | Date of test
[7 empty] | Telephone | +34 93 728 85 00
Tested by Asea Brown Boveri, S.A., Fabrica Motores , 08192 Sant Quirze del Valles , Spain | [6 empty] | Telefax | +34 93 728 85 33
Computer print-out valid without signature.
ABB, Motors and Generators
www abb.com/motors&generators