### Scope

This specification applies to single-phase circuit reclosers with a rated maximum system voltage of up to 27 kV, a maximum continuous current rating of 800 A, and 10 kA symmetrical interrupting rating.

The recloser is designed for pole-mounted installation. All of the unit’s protection functions shall be electronically controlled.

### General

This specification is for a single-phase recloser. The unit must be an ABB OVR-1 or equal. It must utilize magnetic actuation and solid dielectric insulation. Oil or SF6 gas is not allowed. Spring operated and high voltage solenoid mechanisms are not allowed due to maintenance requirements. Control for the recloser shall include the Intelligent Control Device (ICD) or equal.

### Applicable Standards

The recloser and its control must be designed and tested to meet the following standards:

- ANSI/IEEE C37.60 –2003: American National Standard Requirements for Overhead, Padmounted, Dry Vault, and Submersible Automatic Circuit Reclosers and Fault Interrupters for Alternating Current Systems up to 38 kV

- ANSI/IEEE C37.90.1-2002: American National Standard Guide for Surge Withstand Capability Tests

- ANSI/IEEE C37.90.2-1995: IEEE Trial-Use Standard Withstand Capability of Relay Systems to Radiated Electromagnetic Interference from Transceivers

- C37.85–1989: American National Standard Safety Requirement for X-Radiation Limits for AC High-Voltage Power Switchgear

- The manufacturing facility for the recloser must be ISO 9001:2000 and ISO 14001 certified.

### Ratings

## 15 kV 	        24.9 kV          Nom. Voltage

15.5 kV 	           27 kV          Rated Max. Voltage

800 A                   800 A          Rated Continuous Current

10 kA 	           10 kA          Rated Sym. Inter. Current

Rated Withstand Voltages

110 kV	          125 kV         Lightning Impulse (BIL)

50 kV	            60 kV         Power Freq, 1 min (Dry)

45 kV	            50 kV         Power Freq, 10 sec (Wet)

### Construction

- The recloser consists of a cast aluminum-silicon mechanism cabinet and one pole assembly where a vacuum bottle interrupts current.

- The mechanism cabinet is to house a maintenance-free magnetic actuator, which provides the required force to open and close the vacuum pole assembly. The use of a HV solenoid is not acceptable. See details under Mechanism section.

- The recloser shall utilize a hydrophobic cycloaliphatic epoxy (HCEP) solid dielectric for the insulation medium in the pole. SF6 or oil is not acceptable for interruption or insulation purposes.

- The unit shall be designed for 10,000 mechanical or loadbreak (800 A) open/close operations.

- The recloser shall be of a lightweight design, constructed not to exceed 100 lbs. (45 kg) for the pole and 55 lbs (25 kg) for the low-voltage cabinet

- Provisions shall be included for electrical close, and electrical and manual trip.

- Pulling down a yellow handle when in the closed position shall provide mechanical opening.  Mechanical opening will result in unit lockout and mechanical blocking to prevent close.

- A highly visible red/green (opened/closed) indication cup shall be included on the bottom of the actuator housing

- An amber colored indication light shall be included on the bottom floor of the control cabinet and shall illuminate during unit lockout

- Operating temperature range shall be -40 (C (-40 (F) to +70(C (158 (F).

- The mechanism must be accessible though a 5 in (127 mm) x 9 in (229 mm) screw-on panel on the recloser casting.  Use of gasket for prevention of water entry shall be used on both the top of the casting (between casting and pole) and between the casting and the screw-on panel accessing the mechanism.

- The bushing shall be supplied with 1inch (25.4 mm) stud type connectors.

- All parts must be field replaceable.

Mechanism

- The mechanism shall utilize a bi-stable direct drive magnetic actuator capable of fast opening and closing operations with no recharging delay. Bi-stable means that no operating power is required to hold the unit open or closed. The unit must be AC powered through the electronic control or optionally through a rechargeable lead acid battery, allowing fast multiple open-closed-open operations. Reclose delay time on first reclose shall not exceed 0.2 seconds.

Solid Dielectric Insulation

- The recloser shall employ a Hydrophobic Cycloaliphatic Epoxy (HCEP) insulation system and not rely on gaseous or liquid dielectric.

- The insulating dielectric shall be constructed of HCEP, a material that has superior hydrophobicity, which is similar to silicone with the strength of epoxy.

###### Creepage Distances

## 15 kV 	        27 kV

38 in 	        38 in                      H2 – ground (in)

960 mm 	        960 mm                 H2 – ground (mm)

45 in	        45 in                      H1 – H2 (in)

1160 mm	        1160 mm               H1 – H2 (mm)

Vacuum Interrupters

Current interruption shall occur by a vacuum interrupter, providing minimum and even contact wear, long life, and maximum reliability.

###### Current Sensing

- An encapsulated sensor shall provide current sensing. An outdoor mounted current transformer (CT) is not acceptable for current sensing.

- Output from this sensor is sent to the control for current measurement for protection, instrumentation, and metering.

- The current sensor shall be designed not to saturate up to the full interrupting rating of the unit.

- This CT shall not be damaged or open circuited by disconnecting the control cable from an energized recloser.

Mounting Frame

- The recloser shall be provided with a stainless steel mounting frame for pole mounting.

- Mounting bracket must also include brackets for mounting a line and load side surge arrester.

Control Cable

- The recloser is to be supplied with a 10 ft (3 m), 20 ft (6 m), 30 ft (9 m), or 40 ft (12 m) control cable.

- The control cable must be a 12 conductor cable with a PVC jacket and rated -50 oC (-58 (F) to 90 oC (194 (F) and 600V.

### Electronic Control

# Cabinet Construction

- The control cabinet should be stainless steel with a 1500 hour salt spray rating.

- The control cabinet must be of sufficient size to accommodate an electronic control and associated wiring, battery rack and charger (supply optional).

- Use of a gasket for prevention of water entry shall not be required.

Electromechanical Counter

- An electromechanical counter must be included within the control cabinet.

- The electromechanical counter should display the number of times the recloser has operated (1 operation = open-close).

# Battery Backup (Optional)

- The control cabinet may include 4 – 12V, 7.2AH sealed gel lead acid batteries, capable of providing 24 hours of carryover upon loss of AC source power. During this 24-hour period, the battery shall be capable of providing at least 100 open and close operations.

- An external battery charger located within the control cabinet will be required to provide local battery maintenance and monitoring.

- Loss of battery shall not prevent operation when AC is present.

Control Features

The control must have the following pushbuttons with indicating LEDs:

- Open

- Close

- Remote Block

- Alt. Min. Trip

- Non-reclose

The following indicating LEDs are required:

- Control OK

- AC Applied

- Recloser OK

- Pickup

- Overcurrent

- Lockout

The control must have the following protective features:

- 13 recloser Time-Current Curves (TCC): A, B, C, D, E, F, N, R, EF, KF, TF, Y, T

- 6 ANSI TCC curves: Extremely Inverse, Very Inverse, Inverse, Short Time Inverse, Standard Instantaneous, Inverse Instantaneous

- Minimum phase trip value of 20 A.  Pickup range shall be from 20 to 2000 A in 10 A steps

- Selection of number of operations to lockout can be 1, 2, 3, or 4

- The recloser control shall be capable of programming a standard minimum trip (A) setting as well as an alternate setting for seasonal or other alternate applications

- The recloser control shall maintain the capability of carryover electrical power, in the form of capacitors, to allow one open-close-open operation immediately upon loss of electrical power

- If there is insufficient energy available for tripping, the control shall block closing as a safety

- Upon loss of electrical power to the control, the decision to block close or enable reclose shall be determined by the user

- The control will be able to operate the magnetic actuator upon cold-start (following loss of AC power) within 20 seconds

The control must have the following metering capabilities:

Current Values

Phase currents (magnitude only)

Range: 0 to 10 kA primary @ 600 Amp nominal

Accuracy:

- ( 2.0 % of measured value from 0.1x to 1x nominal (i.e., 20 A to 600 A)

- ( 5.0 % of measured value from 1x to 20x nominal (i.e., 600 A to 10 kA)

The control must have the following communication features:

- The control shall be connected directly to a communication device via an RS-232 serial communications link for external access.

- The control must be supplied with ModbusTM ASCII protocol.  DNP 3.0 protocol for SCADA interface is optional through an accessory module that converts from ModbusTM ASCII to DNP 3.0 Level 2.

- All settings shall be enabled and set through the serial link, by way of a simple software program based on the ModbusTM  ASCII protocol message format.

Software Requirements:

The recloser must be supplied with software, free of charge:

- WinICD – software for programming and interfacing with the ICD control

- A 9-pin D type null modem cable is required for connection from RS-232 port to software-loaded PC

# Optional Features and Accessories

- ModbusTM ASCII to DNP 3.0 Level 2 SCADA communications protocol accessory device

- Battery backup power to the recloser control

- Alternate terminal connectors: NEMA 4 hole pad, NEMA 2 hole pad, clamp connectors good for #6-800MCM

- Animal Guards

# Text boxes

Should we remove this.