## Input data (hidden)
Variables
| name | symbol | value | unit
Connection | Operating temperature | T | 22 | °C
| Reference temperature | Tref | 25 | °C
| Temperature coefficient of resistance | a | 5e-06
| Cable Resistivity @ Tref | rho_ref | 1.72e-08 | Ohm.m
| Cable Resistivity @ T | rho | 1.72e-08 | Ohm.m
| Wire cross section | S | 0.08 | mm2
| Resistance between node i and node i-1 | R_dl | =rho*dl_i*1000/S | Ohm
Voltages | Voltage at CU (Voltage start) | V_st | 8.5 | V
| Voltage threshold | V_th | 7.5 | V
| Voltage at node i | Vi | =Vi-1 - DVi | V
| Voltage drop at node i | DVi | =R_dl*Ii-1/1000 | V
Node types | Input modules - absorbed current | DM11 | 120 | mA
| Output modules - absorbed current | DM00 | 65 | mA
| I/O modules - absorbed current | DM10 | 110 | mA
| Open sensor - absorbed current | OCS | 18 | mA
| Closed sensor - absorbed current | SCS | 33 | mA
| Empty | Empty | 0 | mA
[5 empty] | Min | Avg | Max
Initial current | Initial current bus 1 | I_1 | 1000 | mA | 0 | 900 | 1000
| Initial current bus 2 | I_2 | 1000 | mA | 0 | 900 | 1000
| Initial current bus 3 | I_3 | 1000 | mA | 0 | 900 | 1000
[5 empty] | 0 | 2700 | 3000
Bus weight |  | DM11 | 4
|  | DM00 | 4
|  | DM10 | 4
|  | OCS | 1
|  | SCS | 1
|  | Empty | 0

## InSite Bus load simulator
ABB InSite System bus Connectivity check
InSite Bus Position
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
Bus 1 | Cable length from previous node[mm] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| R_dl [Ohm] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Current at node i [mA] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Voltage at node i [V] | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
| Node type [mA] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Node type | SCU100 | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty
| Insite bus Port 1 loading 0mA | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bus length reached [mm] | InSite Bus Position 0: 0; InSite Bus Position 1: 0
Insite bus node capacity | bar: InSite Bus Position 0
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
Bus 2 | Cable length from previous node[mm] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| R_dl [Ohm] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Current at node i [mA] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Voltage at node i [V] | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
| Node type [mA] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Node type | SCU100 | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty
| Insite bus Port 2 loading 0mA | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bus length reached [mm] | 0% 0: 0; 0% 1: 0
Insite bus node capacity | bar: 0% 0
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
Bus 3 | Cable length from previous node[mm] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| R_dl [Ohm] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Current at node i [mA] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Voltage at node i [V] | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
| Node type [mA] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Node type | SCU100 | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty
| Insite bus Port 3 loading 0mA | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bus length reached [mm] | 0% 0: 0; 0% 1: 0
Insite bus node capacity | bar: 0% 0
| T ambient | 0% 1: 22
| SCU power supply loading 0% | 0% 1: 0
Instructions | bar: 0% 0 to 0% 23
1. Set ambient temperature the system will most probably work. You may change this value between operating range (-20 + 60°C) | bar: 0% 0 to 0% 23
2. Fill light blue cells with distance (in mm) between nodes (IO modules or sensors). Distance shall be taken based on the cable lenght and not on air. | bar: 0% 0 to 0% 23
3. Select the type of node | bar: 0% 0 to 0% 23
4. See the results in the node type cell | bar: 0% 0 to 0% 23
If cell is RED colored. Node functionality might not work under the conditions set. Reduce node to node cable lenght or decrease working temperture | bar: 0% 0 to 0% 23
If cell is green colored. Node functionality is guaranteed at the specified temperature | bar: 0% 0 to 0% 23
| SKU | 0% 0: NAME; 0% 1: Description
| 2CCG000245R0001 | 0% 0: DM11; 0% 1: Digital Input module (4 Inputs channels)
| 2CCG000246R0001 | 0% 0: DM00; 0% 1: Digital Output module (4 output channels)
| 2CCG000247R0001 | 0% 0: DM10; 0% 1: Digital Input Output module (2 Input , 2 output )
| CMS-12xx | 0% 0: OCS; 0% 1: Open core Sensor
| CMS-10xx or 20xx | 0% 0: SCS; 0% 1: Solid core sensor