# GENERAL

### The requirements of the Contract, Division [1] [01], and Division [16] [26] apply to work in this Section.

## SECTION INCLUDES

### Low-Voltage Plug-in Busway - 225 to 5000 ampere, 600 VAC; Low-Voltage Feeder Busway-225-6000 ampere, 600 VAC.

## RELATED SECTIONS

## REFERENCES

## The low-voltage plug-in busway and protection devices in this specification are designed and manufactured according to latest revision of the following standards (unless otherwise noted).

### ANSI/IEEE C37.23, Metal-Enclosed Bus and Calculating Losses in Isolated-Bus, Guide for

### ANSI/NEMA BU 1, Busways

### ANSI/NEMA KS 1, Enclosed and Miscellaneous Distribution Equipment Switches (600 Volts)

### ANSI/NFPA 70, National Electrical Code

### CSA C22.2 No. 27, Busways

### NEMA AB 1, Molded Case Circuit Breakers and Molded Case Switches

### NEMA BU1.1, General Instructions for Proper Handling , Installation, Operation, and Maintenance of Busway Rated 600 Volts or Less

### NEMA ICS 2, Industrial Control and Systems: Controllers, Contactors and Overload Relays, Rated Not More Than 2000 Volts AC or 750 Volts DC

## DEFINITIONS

## SYSTEM DESCRIPTION

### Busway shall be a totally enclosed, [indoor] [outdoor] low-impedance system.

### Material and installation shall comply with all applicable codes, recommended practices, and standards of ANSI, IEEE, NEMA, UL, CSA, and ASTA. All busway components shall be UL listed. Arrangements, details, and location shall be as indicated in drawings. Busway shall be tested and conform to IBC-2021 seismic requirements.

### Short circuit rating of fittings with protective devices shall be equal to the lower short circuit rating of the protective device or the busway. Short circuit rating of busway plugs equals the rating of the fuses or circuit breaker used in the plug.

## SUBMITTALS

### Manufacturer shall provide copies of following documents to owner for review and evaluation in accordance with general requirements of Division [1] [01] and Division [16] [26]:

### Product Data on specified product;

### Shop Drawings on specified product;

### Design Data, detailed component data on specified product, such as CT ratios, ratings;

## PROJECT RECORD DOCUMENTS

### Maintain an up-to-date set of Contract documents. Note any and all revisions and deviations that are made during the course of the project.

## OPERATION AND MAINTENANCE DATA

### Manufacturer shall provide copies of installation, operation and maintenance procedures to owner in accordance with general requirements of Division [1] [01] and Division [16] [26].

### Submit operation and maintenance data based on factory and field testing, operation and maintenance of specified product.

## QUALITY ASSURANCE (QUALIFICATIONS)

### Manufacturer shall have specialized in the manufacture and assembly of low-voltage plug-in busway for [50] years.

### Low-voltage plug-in busway shall be listed and/or classified by Underwriters Laboratories in accordance with standards listed in Article 1.03 of this specification.

### Busway shall be qualified for use in seismic areas as follows:

#### IBC-2009, Ss = 2.27g, Sds = 1.51g, Ip = 1.5, for z/h equal to 1 and Ss = 3.68g, Sds = 2.45g, Ip = 1.5, for z/h equal to 0 in accordance with ICC-ES-AC156.

#### Seismic compliance shall be qualified only through shake table testing.  Compliance by calculation is not acceptable.

### Installer has specialized in installing low voltage plug-in busways with [minimum _ years documented experience].

E.	Manufacturer shall have a Quality Management System in place that meets the requirements of ISO 9001:2015

## DELIVERY, STORAGE, AND HANDLING

### Deliver, store, protect, and handle products in accordance with recommended practices listed in manufacturer's Installation and Maintenance Manuals.

### Deliver each low-voltage plug-in busway in individual shipping cartons for ease of handling. Each busway shall be wrapped for protection.

### Inspect and report concealed damage to carrier within specified time.

### Store in a clean, dry space. Maintain factory protection or cover with heavy canvas or plastic to keep out dirt, water, construction debris, and traffic.

### Handle in accordance with NEMA and manufacturer's written instructions to avoid damaging equipment, installed devices, and finish.

## PROJECT CONDITIONS (SITE ENVIRONMENTAL CONDITIONS)

### Follow (standards) service conditions before, during and after busway installation.

### Low-voltage plug-in busways shall be located in well-ventilated areas, free from excess humidity, dust and dirt and away from hazardous materials. Ambient temperature of area will be between minus [30] and plus [40] degrees C. Indoor locations shall be protected to prevent moisture from entering enclosure.

## WARRANTY

### Manufacturer warrants equipment to be free from defects in materials and workmanship for 1 year from date of installation or 18 months from date of purchase, whichever occurs first.

## EXTRA MATERIALS

### Provide [parts] [spares] as indicated in drawings.

### Provide sizes and ratings of spare fuses as indicated in drawings.

## FIELD MEASUREMENTS

### Make all necessary field measurements to verify that equipment shall fit in allocated space in full compliance with minimum required clearances specified in National Electrical Code.

# PRODUCTS

## MANUFACTURER

### ABB products have been used as the basis for design. Other manufacturers' products of equivalent quality, dimensions and operating features may be acceptable, at the Engineer's discretion, if they comply with all requirements specified or indicated in these Contract documents.

## SYSTEMS

### Furnish ABB Reliagear Series™ 225 - 6000 ampere feeder or 225 - 5000 ampere plug-in low-voltage busways (or equal) as indicated in drawings.

## COMPONENTS

### Refer to Drawings for: actual layout and location of equipment and components; current ratings of devices, bus bars, and components; voltage ratings of devices, components and assemblies; and other required details.

### Busway housing shall be extruded aluminum for maximum protection against corrosion from water and other contaminants normally encountered during construction. Housing shall be totally enclosed for protection against mechanical damage and dust accumulation. All hardware shall be plated to prevent corrosion. All outdoor busway shall be rated for NEMA 3R outdoor use and shall comply with IEC IP65/66.  All indoor busway shall be [NEMA 1, complying with IEC IP-40] [drip-proof, complying with IEC IP-43] [splash-proof, complying with IEC IP-54].  All outdoor and indoor splash proof busway shall be provided with Weathershield insulators in the joints.

### All bus bar insulation material shall be epoxy NEMA Class B (130 degree C). Insulation shall be UL rated as self-extinguishing and shall be impervious to acids, alkalis, acetones, machine oils and lubricants commonly found in industrial environments. Manufacturer shall provide test data documenting insulation's impact resistance, chemical resistance, and expected life (50 years).

### Busway shall be rated as indicated in drawings.

### Bus bars shall be [copper] [aluminum].

### Aluminum bus bars shall be silver-plated (standard).    Copper bus bars shall be tin-plated (standard), silver-plating optional.

### Temperature rise at any point in busway shall not exceed 55 degrees C above ambient when operating at rated load current.

### The busway housing may be used in place of an internal ground bar if the manufacturer’s documentation shows that the housing provides a lower resistance ground path than the internal ground bar.  Otherwise an internal [copper][aluminum] ground bar shall be provided that is at least 50% the size and conductivity of main phase bars.  If housing ground path is used, ground path connections shall be tin plated.

### Horizontal busway runs shall be UL listed to hang on 10 foot centers in any position. Vertical busway riser runs shall be supported with spring hangers as shown on plans [with maximum of 16 foot centers].

### NOTE TO SPECIFIER:  THE THROUGH PENETRATION SYSTEM THAT INCLUDES THIS BUSWAY HAS AN F RATING OF 3 HOURS AND A T RATING OF ½ HOUR FOR ALUMINUM BUS AND A T RATING OF 0 HOURS FOR COPPER BUS.  SEE UL CERTIFICATION XHEZ.C-AJ-6003 FOR FURTHER DETAILS AND QUALIFICATIONS.

### Where busway passes through walls or floors, manufacturer shall at user's request provide UL-Listed firestop system [No. 539], GE PENSIL 100 or 500 (or equal).

### Joints shall have plus or minus 1/2 inch adjustability and be the one-bolt removable type. Standard joint bolts shall be provided with a twist off section for initial installation to indicate proper torque during install.  [Optional Joint-Guard Protection System may be used.] See paragraph 2.04, Accessories. Joints shall be able to be made from one side when busway is installed against a wall or ceiling. Plug-in and feeder shall use identical parts. All multi-stacks shall be phase collected.

### Plug-in busway shall be identical to feeder construction and performance except for the following items:

#### Plug in bus shall have [5 outlets per side for 10 total per 10 foot length] [2 outlets per side for 4 total per 10 foot length] All outlets shall be usable simultaneously.

#### Riser bus shall have outlets on only one side and shall have [5 outlets per 10 foot section][2 outlets per 10’ section].  All outlets shall be usable simultaneously.

### Plug-In Unit Safety Device

#### Busway plug-in units shall be of the type(s) and rating listed in Contract. Fusible switching device(s) shall be completely enclosed in a sheet steel housing. Breaker busway plug-in units shall be industrial grade with the breaker totally enclosed in a sheet steel housing and shall be provided with an external operating handle.

#### Shields shall protect stabs and ground plug body before stabs make contact. A grounding terminal shall be inside plug body and shielding to prevent access to live parts when cover is open. A ground stab shall engage ground tab on busway and internal ground bus shall be provided when required.

#### Cover and operating handle shall have provision to padlock in OFF position. Operating handle shall be front mounted on the door of the busway plug-in unit.

#### A releasable cover interlock shall prevent opening cover except when switch is OFF.

#### Operating switch type plug-in units shall have a positive quick-make, quick-break interrupter. Circuit breaker plug-in units shall have thermal magnetic or adjustable electronic trip units as scheduled or specified herein.

### The short circuit rating of the busway, including its integral fittings and protective devices, shall be the lowest of the short circuit ratings of the busway, its fittings or protective devices. For example, a fusible power takeoff rated 200,000 amperes with Class J fuses is installed on a 65,000 ampere rated busway. The rating of this system is 65,000 amperes.

### SPECIFIER NOTE:  INCLUDE THE FOLLOWING WHEN CIRCUIT BREAKERS WITH FULLY ADJUSTABLE TRIP UNITS OR CIRCUIT BREAKERS WITH COMMUNICATIONS CAPABILITY ARE REQUIRED.

### Circuit Breaker plug-in units shall utilize [thermal magnetic], adjustable trip electronic breakers with Dip switch adjustment or adjustable trip electronic with LCD interface for use when communications and metering are required. Provide circuit breaker type as specified herein or indicated on the drawings

### 1.    Circuit breakers shall be [standard 80%] [100%] continuous current rated.

### 2.	Thermal Magnetic circuit breakers shall be the standard unless otherwise specified or noted on the drawings.  Circuit breakers shall be provided with fixed or adjustable thermal magnetic trip units for the size indicated on the schedules or drawings.

3.	Digital electronic circuit breakers with full LSI adjustment shall be provided for [all circuit breaker busplugs][for trip ratings 100A and above]

a.   Digital adjustable trip units shall be ABB EKIP Dip or approved equal

b.   Trip units shall be adjustable from .4 to 1.0 of the circuit breaker sensor rating for long time pickup in .02A increments

c.   Digital electronic trip units shall be provided with fully adjustable short time and instantaneous trip functions.

d.   Provide ground fault trip function where indicated on the drawings.

e.   Digital electronic trip circuit breakers shall be provided with a front mounted USB test    port.

f.  Provide accessories as indicated on schedules or drawings.  These may include shunt trip, bell alarm, aux switches.

4.  Advanced digital electronic trip units shall be ABB EKIP Touch or approved equal.  These shall be utilized when metering and communications are required.

a.   Advanced digital electronic trip circuit breakers shall be provided with a front mounted display, navigation buttons, front USB connector for test and setup and alarm/warning LEDS

b.   Long time shall be adjustable from .4-1.0 of the sensor rating in .01 increments

c.  Short time shall be adjustable from 0.6 – 10.0 of the sensor rating in 0.1 increments

d.  Instantaneous shall be adjustable from 1.5 to 15 of the sensor rating in 0.1 increments

e. Ground fault shall be provided when indicated on the drawings or schedules.  Ground fault pickup shall be adjustable from 0.1 to 1.0 of the sensor rating in .001 increments

f.  [communication shall be provided from the circuit breaker utilizing [modbus RTU}{DeviceNet}{Profinet}{Modbus TCP/IP}{Ethernet IP}Profibus DP}{IEC 61850} protocol]

g.  [ Bluetooth communication shall be provided to remotely monitor and setup the EKIP Touch circuit breaker trip unit]

h.   [Metering shall be provided from the circuit breaker trip unit for current,[voltage, power & energy.  Metering accuracy shall be 1% for current, 0.5% for voltage and 2% for energy and power]

i.  All necessary power supplies and modules shall be provided within the busplug enclosure necessary for metering and/or communication function.

## ACCESSORIES

### Furnish nameplates for each device as indicated in drawings. Color schemes shall be as indicated on drawings.

### Thermal expansion fittings shall be provided for:

#### Runs longer than 150 feet when busway is not free to move at ends of run;

#### When busway run crosses building expansion joint.

3.	Expansion joints shall be +/-1” for fixed long runs and vertical risers and shall be a minimum of +/- 2” when passing building expansion joints.

### Reducer cubicles and special adapter cubicles, as required in drawings.

### Optional Joint-Guard Protection System that uses a "torque sensing bolt". The system shall measure the "elongation of the busway joint bolt". When the bolt loses proper torque, a "red indication shall appear in the bolt head". After re-torquing the bolt, the red indication shall recede and the bolt head shall return to normal color. The system shall be "self renewing" without bolt replacement.]

### Furnish spring hangers as required for vertical risers at each floor penetration and supplementary support location.

### Provide floor and wall flanges at each rated wall or floor penetration as shown on the drawings.

### Furnish end cable or center tap boxes where indicated on the drawings.

## TESTING

### Each busway item shall pass a dielectric withstand test of 5000 VDC for 5 seconds.

## FINISH

### ANSI-61 gray enamel.

# EXECUTION

## EXAMINATION

### Verify that busways are ready to install.

### Verify field measurements are as [shown on Drawings] [instructed by manufacturer].

### Verify that required utilities are available, in proper location and ready for use.

### Beginning of installation means installer accepts conditions.

### Verify that each spring hanger is properly adjusted to support the required weight as described in the busway installation instructions.

## LOCATION

## INSTALLATION

### Additional provisions and editing may be required for this part.

### Install per manufacturer's instructions.

### Install required safety labels.

## FIELD QUALITY CONTROL

### Inspect installed busways for anchoring, alignment, grounding and physical damage.

### Check tightness of all accessible mechanical and electrical connections with calibrated torque wrench. Minimum acceptable values are specified in manufacturer's instructions.

### Megger busways using [500] [1000] [2500] VDC Megger. Check phase to phase, phase to ground. Individual lengths should be at least [3] megohm(s). Entire run should be at least [1] megohm(s). Divide runs over 100 feet long.

### Maintain a dry storage area for the busway before installation.

## ADJUSTING

### Adjust all [circuit breakers] [, ] [switches] [, ] [access doors] [, ] [operating handles] for free [mechanical] [ and / or ] [electrical] operation as described in manufacturer's instructions.

### Adjust circuit breaker trip and time delay settings to values [specified] [determined] by Architect Engineer.

### Adjust all spring hanger supports to values calculated per the installation instructions.

## CLEANING

### Clean interiors of [switchboards] [, ] [panels] [, ] [separate enclosures] to remove construction debris, dirt, shipping materials.

### Repaint scratched or marred exterior surfaces to match original finish.

END OF SECTION