## Telegram 1
68 | Start char
E7 | Length
E7 | Length
68 | Start char
08 | RSP_UD
00 | Primary address
72 | Variable data respond
34 12 00 00 | Serial number | 00001234
42 04 | Manufacturer | ABB
20 | Version
02 | Medium | Electricity
01 | Access number
00 | Status
00 00 | Signature
0E | DIF | Data is 12 digit BCD
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
37 25 26 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
10 | DIFE | Tariff = 1
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
37 25 26 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
20 | DIFE | Tariff = 2
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
30 | DIFE | Tariff = 3
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Tariff = 0
10 | DIFE | Tariff = 4
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
40 | DIFE | Unit=1 => Export
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
89 98 17 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
50 | DIFE | Tariff = 1, Unit = 1 => Export
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
89 98 17 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
60 | DIFE | Tariff = 2, Unit = 1 => Export
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
70 | DIFE | Tariff = 3, Unit = 1 => Export
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Tariff = 0, Unit = 1 => Export
10 | DIFE | Tariff = 4
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
01 | DIF | Data is 8 bit integer
FF | VIF | Next byte is manufacturer specific
93 | VIFE | Active tariff
00 | VIFE | Status: No error
01 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A0 | VIFE | CT numerator
00 | VIFE | Status: No error
01 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A1 | VIFE | VT numerator
00 | VIFE | Status: No error
01 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A2 | VIFE | CT denominator
00 | VIFE | Status: No error
01 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A3 | VIFE | VT denominator
00 | VIFE | Status: No error
01 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A6 | VIFE | Error flags
00 | VIFE | Status: No error
00 00 00 00 00 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A7 | VIFE | Warning flags
00 | VIFE | Status: No error
00 00 00 00 00 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A8 | VIFE | Information flags
00 | VIFE | Status: No error
00 00 3F F0 03 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A9 | VIFE | Alarm flags
00 | VIFE | Status: No error
F8 81 1F 00 00 00 00 00 | Data
0D | DIF | Variable length of data
FD | VIF | Extension of VIF-codes
8E | VIFE | Firmware version
00 | VIFE | Status: No error
08 33 31 2E 31 31 2E 31 41 | Data
0D | DIF | Variable length of data
FF | VIF | Next byte is manufacturer specific
AA | VIFE | Type designation
00 | VIFE | Status: No error
0B 30 30 31 2D 33 31 33 20 34 34 41 | Data
1F | DIF | More data in next telegram
CD | Checksum
16 | End

## Telegram 2
68 | Start char
F2 | Length
F2 | Length
68 | Start char
08 | RSP_UD
00 | Primary address
72 | Variable data respond
34 12 00 00 | Serial number | 00001234
42 04 | Manufacturer | ABB
20 | Version
02 | Medium | Electricity
02 | Access number
00 | Status
00 00 | Signature
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
98 | VIFE | Power fail counter
00 | VIFE | Status: No error
11 00 00 00 | Data
04 | DIF | Data is 32 bit integer
A9 | VIF | Power with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
00 00 00 00 | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
A9 | VIF | Power with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
00 00 00 00 | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
00 00 00 00 | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
00 00 00 00 | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
A9 | VIF | Power with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
00 00 00 00 | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
00 00 00 00 | Data
84 | DIF | Data is 32 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
37 04 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
37 04 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
32 04 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
85 | VIFE | L1 - L2
00 | VIFE | Status: No error
05 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
86 | VIFE | L3 - L2
00 | VIFE | Status: No error
06 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
87 | VIFE | L1 - L3
00 | VIFE | Status: No error
08 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
D9 | VIFE | Ampere with 3 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
D9 | VIFE | Ampere with 3 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
D9 | VIFE | Ampere with 3 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
00 00 00 00 | Data
0A | DIF | Data is 4 digit BCD
FF | VIF | Next byte is manufacturer specific
D9 | VIFE | Frequency with 2 decimals
00 | VIFE | Status: No error
85 49 | Data
1F | DIF | More data in next telegram
E2 | Checksum
16 | End

## Telegram 3
68 | Start char
C1 | Length
C1 | Length
68 | Start char
08 | RSP_UD
00 | Primary address
72 | Variable data respond
34 12 00 00 | Serial number | 00001234
42 04 | Manufacturer | ABB
20 | Version
02 | Medium | Electricity
03 | Access number
00 | Status
00 00 | Signature
02 | DIF | Data is 16 bit integer
FF | VIF | Next byte is manufacturer specific
E0 | VIFE | Power factor with 3 decimals
00 | VIFE | Status: No error
00 00 | Data
02 | DIF | Data is 16 bit integer
FF | VIF | Next byte is manufacturer specific
E0 | VIFE | Power factor with 3 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
00 00 | Data
02 | DIF | Data is 16 bit integer
FF | VIF | Next byte is manufacturer specific
E0 | VIFE | Power factor with 3 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
00 00 | Data
02 | DIF | Data is 16 bit integer
FF | VIF | Next byte is manufacturer specific
E0 | VIFE | Power factor with 3 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
00 00 | Data
02 | DIF | Data is 16 bit integer
FF | VIF | Next byte is manufacturer specific
D2 | VIFE | Phase angle power with 1 decimal
00 | VIFE | Status: No error
00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
30 10 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
90 | DIFE | Tariff = 1
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
30 10 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
A0 | DIFE | Tariff = 2
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
B0 | DIFE | Tariff = 3
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE
50 | DIFE | Tariff = 4, Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
84 06 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
D0 | DIFE | Tariff = 1, Unit=1 => Export
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
84 06 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
E0 | DIFE | Tariff = 2, Unit=1 => Export
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
F0 | DIFE | Tariff = 3, Unit=1 => Export
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
50 | DIFE | Tariff = 4, Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
01 | DIF | Data is 8 bit integer
FF | VIF | Next byte is manufacturer specific
AD | VIFE | Number of elements
00 | VIFE | Status: No error
03 | Data
01 | DIF | Data is 8 bit integer
FF | VIF | Next byte is manufacturer specific
97 | VIFE | Current quadrant
00 | VIFE | Status: No error
00 | Data
01 | DIF | Data is 8 bit integer
FF | VIF | Next byte is manufacturer specific
97 | VIFE | Current quadrant
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
00 | Data
01 | DIF | Data is 8 bit integer
FF | VIF | Next byte is manufacturer specific
97 | VIFE | Current quadrant
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
00 | Data
01 | DIF | Data is 8 bit integer
FF | VIF | Next byte is manufacturer specific
97 | VIFE | Current quadrant
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
00 | Data
1F | DIF | More data in next telegram
9B | Checksum
16 | End

## Telegram 4
68 | Start char
E8 | Length
E8 | Length
68 | Start char
08 | RSP_UD
00 | Primary address
72 | Variable data respond
34 12 00 00 | Serial number | 00001234
42 04 | Manufacturer | ABB
20 | Version
02 | Medium | Electricity
04 | Access number
00 | Status
00 00 | Signature
81 | DIF | Data is 8 bit integer
40 | DIFE | Unit=1 => Output 1
FD | VIF | Extension of VIF-codes
9A | VIFE | Digital output
00 | VIFE | Status: No error
00 | Data
81 | DIF | Data is 8 bit integer
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Output 2
FD | VIF | Extension of VIF-codes
9A | VIFE | Digital output
00 | VIFE | Status: No error
00 | Data
81 | DIF | Data is 8 bit integer
C0 | DIFE | Unit=1
40 | DIFE | Unit=3 => Output 3
FD | VIF | Extension of VIF-codes
9B | VIFE | Digital output
00 | VIFE | Status: No error
00 | Data
81 | DIF | Data is 8 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Input 4
FD | VIF | Extension of VIF-codes
9B | VIFE | Digital input
00 | VIFE | Status: No error
00 | Data
C1 | DIF | Storage no = 1, Data is 8 bit integer
C0 | DIFE | Unit=1
40 | DIFE | Unit=3 => Input 3
FD | VIF | Extension of VIF-codes
9B | VIFE | Digital input
00 | VIFE | Status: No error
00 | Data
C1 | DIF | Storage no = 1, Data is 8 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Input 4
FD | VIF | Extension of VIF-codes
9B | VIFE | Digital input
00 | VIFE | Status: No error
00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=0
40 | DIFE | Unit=2 => Counter 2
FD | VIF | Extension of VIF-codes
E1 | VIFE | Cumulating counter
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Counter 4
FD | VIF | Extension of VIF-codes
E1 | VIFE | Cumulating counter
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
0E | DIF | Data is 12 digit BCD
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
F2 | VIFE | Resettable register
00 | VIFE | Status: No error
37 25 26 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
40 |  | Unit=1 => Export
84 |  | Energy with 2 decimals
FF |  | Next byte is manufacturer specific
F2 |  | Resettable register
00 | VIFE | Status: No error
89 98 17 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 |  | Unit=0
40 |  | Unit=2 => Reactive
84 |  | Energy with 2 decimals
FF |  | Next byte is manufacturer specific
F2 |  | Resettable register
00 | VIFE | Status: No error
30 10 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 |  | Unit=1 => Export
40 |  | Unit=2 => Reactive
84 |  | Energy with 2 decimals
FF |  | Next byte is manufacturer specific
F2 |  | Resettable register
00 | VIFE | Status: No error
84 06 00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF |  | Next byte is manufacturer specific
F1 |  | Reset counter for energy
00 | VIFE | Status: No error
00 00 00 00 | Data
84 | DIF | Data is 32 bit integer
40 |  | Unit=1 => Export
FF |  | Next byte is manufacturer specific
F1 |  | Reset counter for energy
00 | VIFE | Status: No error
00 00 00 00 | Data
84 | DIF | Data is 32 bit integer
80 |  | Unit=0
40 |  | Unit=2 => Reactive
FF |  | Next byte is manufacturer specific
F1 |  | Reset counter for energy
00 | VIFE | Status: No error
00 00 00 00 | Data
84 | DIF | Data is 32 bit integer
C0 |  | Unit=1 => Export
40 |  | Unit=2 => Reactive
FF |  | Next byte is manufacturer specific
F1 |  | Reset counter for energy
00 | VIFE | Status: No error
00 00 00 00 | Data
0E | DIF | Data is 12 digit BCD
FF | VIF | Next byte is manufacturer specific
F9 | VIFE | Extension of manufacturer specific VIFE-codes
C4 | VIFE | Energy in CO2, kg with 3 decimals
00 | VIFE | Status: No error
76 53 62 02 00 00 | Data
0E | DIF | Data is 12 digit BCD
FF | VIF | Next byte is manufacturer specific
F9 | VIFE | Extension of manufacturer specific VIFE-codes
C9 | VIFE | Energy in currency with 2 decimals
00 | VIFE | Status: No error
38 25 26 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A4 | VIFE | CO2 conversion factor (kg * 10-3 /kWh)
00 | VIFE | Status: No error
E8 03 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A5 | VIFE | Currency conversion factor (curr * 10-3 /kWh)
00 | VIFE | Status: No error
E8 03 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
24 25 26 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
80 98 17 00 00 00 | Data
1F | DIF | More data in next telegram
47 | Checksum
16 | End

## Telegram 5
68 | Start char
F7 | Length
F7 | Length
68 | Start char
08 | RSP_UD
00 | Primary address
72 | Variable data respond
34 12 00 00 | Serial number | 00001234
42 04 | Manufacturer | ABB
20 | Version
02 | Medium | Electricity
05 | Access number
00 | Status
00 00 | Signature
0E | DIF | Data is 12 digit BCD
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
48 00 26 00 00 00 | Data
0E | DIF | Data is 12 digit BCD
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
57 05 26 00 00 00 | Data
0E | DIF | Data is 12 digit BCD
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
76 66 17 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
40 | DIFE | Unit=1 => Export
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
07 81 17 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
40 | DIFE | Unit=1 => Export
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
62 84 17 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
40 | DIFE | Unit=1 => Export
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
64 80 25 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
72 00 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
85 00 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
52 11 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
39 01 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
89 01 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
40 | DIFE | Unit=2 => Reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
30 06 00 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
39 00 26 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
48 05 26 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
71 66 17 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
98 80 17 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
49 84 17 00 00 00 | Data
8E | DIF | Data is 12 digit BCD
C0 | DIFE | Unit=1 => Export
80 | DIFE | Unit=0
40 | DIFE | Unit=4 => Apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
59 80 25 00 00 00 | Data
1F | DIF | More data in next telegram
0F | Checksum
16 | End

## Telegram 6
68 | Start char
CE | Length
CE | Length
68 | Start char
08 | RSP_UD
00 | Primary address
72 | Variable data respond
34 12 00 00 | Serial number | 00001234
42 04 | Manufacturer | ABB
20 | Version
02 | Medium | Electricity
06 | Access number
00 | Status
00 00 | Signature
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 6 = Net
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
D8 42 01 00 00 00 00 00 | Data
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 6 = Net
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
15 40 01 00 00 00 00 00 | Data
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 6 = Net
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
AE 40 01 00 00 00 00 00 | Data
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 6 = Net
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
15 C2 FE FF FF FF FF FF | Data
87 | DIF | Data is 64 bit integer
C0 | DIFE | Unit=1 =>
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 7 = Net reactive
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
5A 01 00 00 00 00 00 00 | Data
87 | DIF | Data is 64 bit integer
C0 | DIFE | Unit=1 =>
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 7 = Net reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
BD FF FF FF FF FF FF FF | Data
87 | DIF | Data is 64 bit integer
C0 | DIFE | Unit=1 =>
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 7 = Net reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
99 FF FF FF FF FF FF FF | Data
87 | DIF | Data is 64 bit integer
C0 | DIFE | Unit=1 =>
C0 | DIFE | Unit=2 =>
40 | DIFE | Unit=4 => 7 = Net reactive
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
0A 02 00 00 00 00 00 00 | Data
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=8 => Net apparent
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
D3 42 01 00 00 00 00 00 | Data
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=8 => Net apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
15 40 01 00 00 00 00 00 | Data
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=8 => Net apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
B2 40 01 00 00 00 00 00 | Data
87 | DIF | Data is 64 bit integer
80 | DIFE | Unit=0
80 | DIFE | Unit=0
80 | DIFE | Unit=0
40 | DIFE | Unit=8 => Net apparent
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
15 C2 FE FF FF FF FF FF | Data
0F | DIF | No more data in next telegram
58 | Checksum
16 | End