## Telegram 1
68 | Start char
B7 | Length
B7 | Length
68 | Start char
08 | RSP_UD
00 | Primary address
72 | Variable data respond
33 53 10 00 | Serial number | 00001234
42 04 | Manufacturer | ABB
20 | Version
02 | Medium | Electricity
02 | Access number
00 | Status
00 00 | Signature
0E | DIF | Data is 12 digit BCD
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A0 | VIFE | CT numerator
15 | VIFE | Status: No data available
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A1 | VIFE | VT numerator
15 | VIFE | Status: No data available
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A2 | VIFE | CT denominator
15 | VIFE | Status: No data available
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A3 | VIFE | VT denominator
15 | VIFE | Status: No data available
00 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A6 | VIFE | Error flags
00 | VIFE | Status: No error
00 00 00 00 00 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A7 | VIFE | Warning flags
00 | VIFE | Status: No error
00 00 00 00 00 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A8 | VIFE | Information flags
00 | VIFE | Status: No error
00 00 00 00 00 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A9 | VIFE | Alarm flags
00 | VIFE | Status: No error
00 00 00 00 00 00 00 00 | Data
0D | DIF | Variable length of data
FD | VIF | Extension of VIF-codes
8E | VIFE | Firmware version
00 | VIFE | Status: No error
07 30 2E 34 2E 30 31 42 | Data
0D | DIF | Variable length of data
FF | VIF | Next byte is manufacturer specific
AA | VIFE | Type designation
00 | VIFE | Status: No error
0B 30 30 31 2D 33 31 33 20 31 32 42 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
98 | VIFE | Power fail counter
00 | VIFE | Status: No error
02 00 00 00 | Data
04 | DIF | Data is 32 bit integer
A9 | VIF | Power with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
8A 02 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
D9 | VIFE | Ampere with 3 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
00 00 00 00 | Data
0A | DIF | Data is 4 digit BCD
FF | VIF | Next byte is manufacturer specific
D9 | VIFE | Frequency with 2 decimals
00 | VIFE | Status: No error
82 49 | Data
02 | DIF | Data is 16 bit integer
FF | VIF | Next byte is manufacturer specific
E0 | VIFE | Power factor with 3 decimals
00 | VIFE | Status: No error
00 00 | Data
01 | DIF | Data is 8 bit integer
FF | VIF | Next byte is manufacturer specific
AD | VIFE | Number of elements
00 | VIFE | Status: No error
01 | Data
81 | DIF | Data is 8 bit integer
40 | DIFE | Unit=1 => Output 1
FD | VIF | Extension of VIF-codes
9A | VIFE | Digital output
00 | VIFE | Status: No error
00 | Data
0F | DIF | No more data in next telegram
C8 | Checksum
16 | End