SPECIFICATION

FOR

VACUUM PRESSURE IMPREGNATED (VPI) TRANSFORMER

INDOOR AND OUTDOOR VENTILATED

- Scope

1.1	The ABB Inc. Vacuum Pressure Impregnated (VPI) transformer design is the basis for this specification. Other approved manufacturers are ______________________________.

  - This specification together with the applicable Transformer Data Sheet provides the technical requirements for the design, manufacture and test of secondary unit substation transformers. The service conditions shall be as specified in Usual Service Conditions section of C57.12.01.

  - This specification covers only the general requirements of the transformer. The specific requirements will be given on detailed on the Transformer Data Sheet.

- Codes and Standards

2.1	The ventilated dry-type transformers and protection devices in this specification are designed and manufactured according to latest revision of the following standards (unless otherwise noted).

2.1.1	IEEE C57.12.01, General Requirements for Dry-Type Distribution and Power Transformers Including Those with Solid Cast and / or Resin-Encapsulated Windings

2.1.2	ANSI C57.12.51, Requirements for Ventilated Dry-Type Power Transformers, 501 KVA and Larger, Three-Phase with High-Voltage 601 to 34 500 Volts, Low Voltage 208Y/120 to 4160Volts

2.1.3	ANSI C57.12.55, Dry-Type Transformers in Unit Installations, Including Unit Substations –Conformance Standard

2.1.4	ANSI/IEEE C57.98, Impulse Tests, Guide for Transformer (Appendix to ANSI/IEEE

C57.12.90)

2.1.5	ANSI/NFPA 70, National Electrical Code

2.1.6	IEEE C57.12.91, Test Code for Dry-Type Distribution and Power Transformers

2.1.7	IEEE C57.94, Recommended Practice for Installation, Application, Operation and Maintenance of Dry-Type General Purpose Distribution and Power Transformers

2.1.8	IEEE C57.96, Guide for Loading Dry-Type Distribution and Power Transformers

    - NEMA ST 20, Dry Type Transformers for General Applications

    - American Society of Testing and Materials (ASTM)

    - National Electrical Code (NEC)

  - It shall be the Seller’s responsibility to be, or to become, knowledgeable of the requirements of these Codes and Standards. Any required changes or alterations to the equipment to meet the Codes and Standards requirements shall be at the expense of the Seller.

  - Equipment proposed by the Seller that cannot fully meet the requirements of this specification shall have all exceptions clearly stated in the proposal. No exception shall be allowed, unless approved by the Buyer in writing.

3.0		Quality Assurance

  - The manufacturer shall a well-documented quality assurance program, which includes procedures for all activities in order entry, design, material procurement, manufacturing processes, testing, shipping and post shipment.

  - The manufacturer shall have specialized in the design, manufacture and assembly of dry-type distribution transformers for a minimum of {25} years.

  - The transformers shall be manufactured by a company, which is certified to ISO, 9001:1994, EN ISO 9001:1994; BS EN ISO 9001:1994; ANSI/ASQC Q9001: 1994 for design and manufacture of Power, Distribution and Specialty Dry Type Transformers.  A certificate of Compliance to this requirement shall be provided with the proposal.

  - The test floor shall have a documented calibration program. All equipment shall receive regular calibrations. Calibration standards shall be traceable to National Bureau of Standards. Records of all equipment calibration shall be made available to the Buyer upon request.

  - Measured values of electric power, voltage, current, resistance, and temperatures are used in the calculations of reported data.  To ensure sufficient accuracy in the measured and calculated date the test system accuracy requirements listed in ANSI C57.12.01 Table 3 shall be met as a minimum.

4.0		Transformer Technical Requirements

  - Definitions

    - System Description

      - The transformer shall be of dry type vacuum pressure impregnated construction, the preferred open-wound dry type technology, and shall be mounted in a suitably ventilated (indoor, outdoor) enclosure.

      - Primary terminations shall be [stub bus inside transformer enclosure/close-coupled to high voltage switchgear/cable connected in air-filled terminal chamber].

      - Secondary terminations shall be [stub bus inside transformer enclosure/close-coupled to low voltage switchgear / busway or cable connected in air-filled terminal chambers].

  - Core Characteristics

    - The transformer core shall be constructed of high grade non-aging silicon steel laminations with high magnetic permeability and low hysteresis and eddy current losses.  Magnetic flux densities are to be kept well below the saturation point.  A step-lap mitered core joint shall be used to minimize losses, exciting currents and sound levels.  The core laminations shall be clamped together with heavy steel members.

  - Temperature Rise

    - The average temperature rise of the transformer windings shall be rated at (80°C, 115°C, 150°C) and shall be built utilizing Class 220°C insulations, regardless of the temperature rise specified.  The transformer shall not exceed the specified temperature rise when the unit is operated continuously at full nameplate rating.  The transformer shall be capable of carrying 100% of the nameplate rating in a 30°C average, not to exceed 40°C maximum ambient in any 24 hour period.

  - Coil Characteristics

    - The high voltage and low voltage windings shall be constructed using (copper, aluminum) conductors.  The conductors shall be insulated with a 220°C insulation.  Transformer windings, insulation class 1.2 kV (600v) and below, shall be wound using foil or sheet conductors.  A sheet wound coil allows free current distribution within the axial width of the conductor/coil to essentially eliminate axail forces under short circuit.

Transformer windings, insulation class 2.5 kV (2400v) and above, shall be wound using wire conductors.  The high voltage winding shall be wound over the low voltage winding with sufficient mechanical bracing to prevent movement during fault conditions and sufficient solid Class 220°C insulation to isolate the high voltage winding dielectric potential from the low voltage windings.

    - Taps Transformer primary winding shall have [{four 2-1/2 percent full capacity taps, two above and two below} rated nominal voltage. No load tap connections shall be made by re-connectable links on the face of the primary winding and shall be located behind removable panels on the front of transformer enclosure. Taps shall be for de-energized operation only{no taps}].

  - Core and Coil Assembly

    - After installation of windings on core and stacking of the top yoke core steel, core and coil assembly is to be secured with a rigid frame.  Primary and secondary coordination bus assemblies, as required for connection to associated switchgear are to be of (welded, bolted) construction.

  - Vacuum Pressure Impregnation Process

    - The coils and all clamping structure and buswork shall be assembled on the core, and then dried at atmospheric pressure in an oven through which hot air is continuously circulated.  The totally assembled core and coil assembly shall be vacuum pressure impregnated in polyester varnish. The total VPI process shall apply a one (1) cycle polyester protective shield of varnish to the coils and a protective shield to the bus, core and support structure.  The varnish shall be cured on the core and coil assembly following an established temperature vs. time baking cycle in a hot air circulating oven.  The VPI process shall effectively impregnate the entire core and coil assembly that results in a unit which is virtually impermeable to moisture, dust, dirt, salt air and other industrial contaminants.

  - Dielectric Withstand

    - The impulse rating of the transformer must equal or exceed the basic impulse level specified by ANSI for the applicable voltage class.  The basic impulse level shall be inherent to the winding design and is to be obtained without the use of supplemental surge arrestors.

  - Vibration Isolation

    - The transformer shall have vibration isolation pads installed between core and coil assembly and enclosure base structures to prevent the transmission of structure borne vibration.

  - Enclosure

    - The enclosure shall be constructed of heavy gauge sheet steel and shall be finished in ANSI 61 paint color applied using an electrostatically deposited dry powder paint system.  All ventilating openings shall be in accordance with NEMA and the NEC standards for ventilated enclosures.  The base of the enclosure shall be furnished with ground pads located on opposite diagonal corners.  The base shall have jacking pads and shall be constructed of heavy steel members to permit skidding or rolling in any direction.  The core shall be visibly grounded to the enclosure frame by means of a flexible grounding strap.

      - Optional - Transformer shall be certified to meet California Building Code (CBC) Zone 4 seismic requirements with seismic table validation.

      - Optional - Outdoor enclosures shall be certified and constructed to withstand a 110 mph wind load test and shall provide NEMA 3R protection against rain, sleet and external ice construction.

  - Nameplate

    - Transformer shall be furnished with a non-corrosive diagrammatic nameplate per ANSI C57.12.01, permanently attached with non-corrosive hardware.  The diagrammatic nameplate shall include the name of the manufacturer of the transformer as well as the location where the transformer was manufactured and tested.  In addition, the transformer manufacturer and location of manufacture is to be supplied at the time of quotation.

  - Forced Air Cooling

    - Forced air cooling, when required, shall increase the continuous self cooled rating of the transformer by 33 1/3% for units rated 3750 kVA and below and 25% for units 3751 kVA and larger.  The FA increase shall be possible with forced cooling without exceeding the specified maximum temperature rise.  The forced air cooling shall be regulated automatically by sensors placed in the low voltage winding’s air ducts.  Forced air cooling shall include: three phase electronic digital temperature monitor, fans, control wiring, control panel with test switch, indicating lights, alarm and alarm silencing switch.

  - Optional Overload Capabilities

    - When 80°C and 115°C winding temperature rise are specified, they can be designed with inherent overload capabilities.  An 80°C rise unit would be capable of continuous operation at 35% above nameplate rating and a 115°C rise unit would be capable of continuous operation at 17% above nameplate rating.  This overload capability would be achieved on the AA and FA rating and could be accomplished by allowing the transformers’ ultimate rise to be 150°C.  Customer specification must define the high capacity overloads.

- Test

  - After completion, each transformer shall undergo the following routine production tests per ANSI C57.12.01 and ANSI C57.12.91.  Testing shall be accomplished using calibrated test equipment, which have recorded accuracy traceable to National Institute of Standards Technologies (NIST).  Certification of Calibration shall be provided with test reports if requested.

    - Megger

    - Ratio

    - Resistance

    - Phase relation

    - Load Loss, Impedance and Regulation

    - No Load Loss and Excitation Current

    - 100% QC Impulse Test

    - Applied Potential Test

    - Induced Potential Test

  - In addition to routine testing a 100% QC Impulse test shall be performed on each transformer furnished.

  - A temperature rise test shall be performed on the first unit of each new design.

    - The temperature rise of the windings at rated KVA loading shall not exceed maximum rise specified during operation at 30 degrees C average ambient, which does not exceed 40 degrees C in a 24 hour period.

  - A sound level test shall be performed on the first unit of each new design.

    - Sound level shall not exceed the maximum specified by ANSI C57.12.01 for applicable KVA size of dry-type transformer.

  - The core and coil design and construction techniques shall be verified by a full short circuit test on similar or larger units in accordance with applicable ANSI standards.

- Accessories

  - Standard transformer accessories shall include:

    - Diagrammatic instruction nameplate

    - Provisions for  lifting and jacking

    - Removable case panel for access to HV taps

    - Stainless steel ground pads

    - Line voltage adjustment taps, 2 - FCAN and 2 - FCBN, All at 2 ½%

- Documentation

  - Manufacturer shall provide copies of following documents to owner for review and evaluation.

    - Outline, nameplate and connection diagram drawings.

    - Installation maintenance and operating instructions

    - A certified test report containing minimum information per IEEE C57.12.91

    - Spare parts list

# Transformer Data Sheet: (Circled items are specific to this project.)

### Customer Name: _______________________Project/Quote Number: ________ Item No.___

KVA Rating:	112.5	225	300	500	750	1000	1500	2000	2500	3000		3750	5000	7500	10000	OTHER (_______)

Frequency:	50 HZ	60 HZ

Impedance:	5.75%		OTHER(________)

Winding Temperature Rise: 	 150 (C 		115 (C		80 (C	OTHER (_______)

Primary Voltage: (kV)	2.4	4.16	12.47	13.2	13.8	24.9	34.5	OTHER (_______)

Primary Taps:	Standard (( 2-2 ½) 	OTHER (__________)

Primary BIL*: (kV)	Std.	20	30	45	60	75	95	110	125	150			OTHER (________)

Primary Connection:	Delta	Wye

Primary Termination:	Stub Bus	Switchgear Close Coupled	 	Air Terminal Chamber

ANSI Segment:		1	2	3	4

Secondary Voltage: 	208	240	480	600	2400	4160	OTHER (_______)

# Secondary BIL*:  (kV)	Std.	10	20	30	45	60	OTHER (_______)

Secondary Connection: 	Delta	Wye

Secondary Termination: 	Stub Bus	Switchgear Close Coupled		Air Terminal Chamber

ANSI Segment:		1	2	3	4

Application Location:	Indoor NEMA 1____		Outdoor NEMA 3R____

Forced Air Rating:	AA	AA/FA		AA/FFA		OTHER (_______)

Sound Level: 	Standard ____	Special ________

Special Tests:	Witness	__;	Temperature __	;	ANSI Impulse __ 	ANSI Sound __

OTHER (___________)

Drawings: 	Record __;	Approval ___;		Hard Copy__		Electronic DXF File__

#### Other Special Instructions:

______________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

### *Standard/Optional Basic Impulse Levels

Insulation Class		Standard BIL		Optional BIL

1.2	10	20/30

2.5	20	30/45/60

5.0	30	45/60

8.7	45	60/75/95

15.0	60	95/110

25.0	110	125/150

34.5	150

Specification  VPI001