## Telegram 1
68 | Start char
86 | Length
86 | Length
68 | Start char
08 | RSP_UD
00 | Primary address
72 | Variable data respond
41 01 04 00 | Serial number | 00040141
42 04 | Manufacturer | ABB
20 | Version
02 | Medium | Electricity
01 | Access number
00 | Status
00 00 | Signature
0E | DIF | Data is 12 digit BCD
84 | VIF | Energy with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A0 | VIFE | CT numerator
15 | VIFE | Status: No data available
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A1 | VIFE | VT numerator
15 | VIFE | Status: No data available
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A2 | VIFE | CT denominator
15 | VIFE | Status: No data available
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FF | VIF | Next byte is manufacturer specific
A3 | VIFE | VT denominator
15 | VIFE | Status: No data available
00 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A6 | VIFE | Error flags
00 | VIFE | Status: No error
00 00 00 00 00 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A7 | VIFE | Warning flags
00 | VIFE | Status: No error
00 00 00 00 00 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A8 | VIFE | Information flags
00 | VIFE | Status: No error
00 00 00 00 00 00 00 00 | Data
07 | DIF | Data is 64 bit integer
FF | VIF | Next byte is manufacturer specific
A9 | VIFE | Alarm flags
00 | VIFE | Status: No error
00 00 00 00 00 00 00 00 | Data
0D | DIF | Variable length of data
FD | VIF | Extension of VIF-codes
8E | VIFE | Firmware version
00 | VIFE | Status: No error
08 31 33 2E 31 31 2E 31 41 | Data
0D | DIF | Variable length of data
FF | VIF | Next byte is manufacturer specific
AA | VIFE | Type designation
00 | VIFE | Status: No error
0B 30 30 31 2D 33 31 31 20 33 34 41 | Data
1F | DIF | More data in next telegram
86 | Checksum
16 | End

## Telegram 2
68 | Start char
C4 | Length
C4 | Length
68 | Start char
08 | RSP_UD
00 | Primary address
72 | Variable data respond
41 01 04 00 | Serial number | 00040141
42 04 | Manufacturer | ABB
20 | Version
02 | Medium | Electricity
02 | Access number
00 | Status
00 00 | Signature
04 | DIF | Data is 32 bit integer
A9 | VIF | Power with 2 decimals
00 | VIFE | Status: No error
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
A9 | VIF | Power with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
16 09 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
16 09 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
16 09 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
85 | VIFE | L1 - L2
00 | VIFE | Status: No error
06 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
86 | VIFE | L3 - L2
00 | VIFE | Status: No error
0B 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
C8 | VIFE | Volt with 1 decimal
FF | VIFE | Next byte is manufacturer specific
87 | VIFE | L1 - L3
00 | VIFE | Status: No error
0C 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
D9 | VIFE | Ampere with 3 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
D9 | VIFE | Ampere with 3 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
00 00 00 00 | Data
04 | DIF | Data is 32 bit integer
FD | VIF | Extension of VIF-codes
D9 | VIFE | Ampere with 3 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
00 00 00 00 | Data
0A | DIF | Data is 4 digit BCD
FF | VIF | Next byte is manufacturer specific
D9 | VIFE | Frequency with 2 decimals
00 | VIFE | Status: No error
83 49 | Data
02 | DIF | Data is 16 bit integer
FF | VIF | Next byte is manufacturer specific
E0 | VIFE | Power factor with 3 decimals
00 | VIFE | Status: No error
00 00 | Data
01 | DIF | Data is 8 bit integer
FF | VIF | Next byte is manufacturer specific
AD | VIFE | Number of elements
00 | VIFE | Status: No error
03 | Data
81 | DIF | Data is 8 bit integer
40 | DIFE | Unit=1 => Output 1
FD | VIF | Extension of VIF-codes
9A | VIFE | Digital output
00 | VIFE | Status: No error
00 | Data
0E | DIF | Data is 12 digit BCD
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
81 | VIFE | L1
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
0E | DIF | Data is 12 digit BCD
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
82 | VIFE | L2
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
0E | DIF | Data is 12 digit BCD
84 | VIF | Energy with 2 decimals
FF | VIFE | Next byte is manufacturer specific
83 | VIFE | L3
00 | VIFE | Status: No error
00 00 00 00 00 00 | Data
0F | DIF | More data in next telegram
93 | Checksum
16 | End